## Table of Results
PE Pipe or Tube
Unique Name | Status | Length (*) | Inside Diameter (*) | Design Velocity (*) | Design Pressure Gradient (*) | Heat Loss Model | Heat Transfer Coeff (U Value) | Average Soil Temperature (*) | Sizing Pressure Gradient (Pa/m) | Wall Shear Stress (Pa a) | Fluid Shear Rate (in s-1) | Out Stagnation Pressure (Pa a) | In Velocity (m/s) | In Stagnation Pressure (Pa a) | Element Type | User Number | Sizing Velocity (m/s) | Economic Velocity (m/s) | Pressure Gradient (Pa/m) | Friction Loss (Pa) | Flow at NTP (m3/h) | Flow at STP (m3/h) | Flow (kg/s)
| On | 20 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 477858.4 | 6.36 | 478182.5 | PE Pipe or Tube | -150 | 0 | 9.44 | 16.2 | 324.1 | 1362.303 | 1437.416 | 0.5
| On | 20 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 471922.2 | 18.8 | 474535.8 | PE Pipe or Tube | -149 | 0 | 9.41 | 130.7 | 2613.6 | 3964.503 | 4183.091 | 1.4
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 527506.7 | 42.16 | 536684.9 | PE Pipe or Tube | -148 | 0 | 8.84 | 734.3 | 9178.2 | 10090.02 | 10646.345 | 3.6
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 568411.6 | 48.15 | 581444.3 | PE Pipe or Tube | -147 | 0 | 8.58 | 1042.6 | 13032.8 | 12482.173 | 13170.393 | 4.5
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 486109.6 | 21.96 | 488405.8 | PE Pipe or Tube | -146 | 0 | 9.28 | 183.7 | 2296.3 | 4800.258 | 5064.926 | 1.7
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 506472.5 | 34.92 | 512486.8 | PE Pipe or Tube | -145 | 0 | 9.03 | 481.1 | 6014.4 | 7993.181 | 8433.895 | 2.9
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102775 | 47.59 | 104296.7 | PE Pipe or Tube | -119 | 0 | 14.76 | 304.3 | 1521.7 | 1048.429 | 1106.236 | 0.4
| On | 1 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 483666.8 | 15.52 | 483760.1 | PE Pipe or Tube | -118 | 0 | 9.37 | 93.3 | 93.3 | 3363.063 | 3548.49 | 1.2
| On | 1 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 485559.6 | 26.44 | 485832.6 | PE Pipe or Tube | -117 | 0 | 9.25 | 273 | 273 | 5746.858 | 6063.718 | 2.1
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 103099.6 | 52.46 | 104950.3 | PE Pipe or Tube | -114 | 0 | 14.71 | 370.1 | 1850.7 | 1161.434 | 1225.471 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 513897.8 | 10.19 | 514238.3 | PE Pipe or Tube | -113 | 0 | 9.22 | 68.1 | 340.5 | 1109.988 | 1171.189 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102868.4 | 49.05 | 104484.3 | PE Pipe or Tube | -112 | 0 | 14.74 | 323.2 | 1615.9 | 1082.075 | 1141.737 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 464398.7 | 10.06 | 464700.8 | PE Pipe or Tube | -108 | 0 | 9.5 | 60.4 | 302.1 | 990.423 | 1045.032 | 0.4
| On | 0 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102618.7 | 45.63 | 102637 | PE Pipe or Tube | -107 | 0 | 14.83 | 18338.1 | 18.3 | 989.592 | 1044.154 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 494186.8 | 10.14 | 494512.1 | PE Pipe or Tube | -106 | 0 | 9.33 | 65 | 325.2 | 1062.419 | 1120.997 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 480595.6 | 10.11 | 480910.3 | PE Pipe or Tube | -105 | 0 | 9.4 | 62.9 | 314.7 | 1029.588 | 1086.355 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102733.2 | 46.93 | 104213.2 | PE Pipe or Tube | -104 | 0 | 14.76 | 296 | 1480.1 | 1033.029 | 1089.987 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 484276.5 | 10.12 | 484594.1 | PE Pipe or Tube | -103 | 0 | 9.38 | 63.5 | 317.5 | 1038.483 | 1095.741 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 480931.3 | 10.11 | 481246.2 | PE Pipe or Tube | -102 | 0 | 9.4 | 63 | 314.9 | 1030.399 | 1087.211 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 476582.1 | 10.1 | 476893.7 | PE Pipe or Tube | -101 | 0 | 9.43 | 62.3 | 311.6 | 1019.883 | 1076.116 | 0.4
| On | 30 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 476597.5 | 10.08 | 478465.2 | PE Pipe or Tube | -100 | 0 | 9.42 | 62.3 | 1867.7 | 1021.491 | 1077.813 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 481561.2 | 10.11 | 481876.6 | PE Pipe or Tube | -99 | 0 | 9.4 | 63.1 | 315.4 | 1031.923 | 1088.82 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102780.2 | 47.67 | 104307.4 | PE Pipe or Tube | -98 | 0 | 14.76 | 305.4 | 1527.2 | 1050.352 | 1108.264 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 497138.9 | 10.15 | 497466.4 | PE Pipe or Tube | -97 | 0 | 9.31 | 65.5 | 327.5 | 1069.559 | 1128.53 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 521382.7 | 10.21 | 521729 | PE Pipe or Tube | -96 | 0 | 9.18 | 69.3 | 346.3 | 1128.049 | 1190.245 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 559868.8 | 10.29 | 560244.8 | PE Pipe or Tube | -95 | 0 | 8.99 | 75.2 | 376 | 1220.759 | 1288.067 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 103252.8 | 54.57 | 105259.4 | PE Pipe or Tube | -94 | 0 | 14.69 | 401.3 | 2006.6 | 1211.283 | 1278.068 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102905.3 | 49.62 | 104559.3 | PE Pipe or Tube | -93 | 0 | 14.74 | 330.8 | 1654 | 1095.202 | 1155.587 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 103128.9 | 52.89 | 105010.6 | PE Pipe or Tube | -92 | 0 | 14.7 | 376.3 | 1881.7 | 1171.394 | 1235.981 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 857063.9 | 126.72 | 961325 | PE Pipe or Tube | -91 | 0 | 7.3 | 20852.2 | 104261.1 | 23958.059 | 25279.016 | 8.6
| On | 5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 477957.2 | 12.29 | 478243.5 | PE Pipe or Tube | -85 | 0 | 9.46 | 57.3 | 286.3 | 2602.199 | 2745.675 | 0.9
| On | 40 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 468428.6 | 19.6 | 477539.3 | PE Pipe or Tube | -84 | 0 | 9.45 | 227.8 | 9110.8 | 1980.015 | 2089.186 | 0.7
| On | 40 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 468084.9 | 10.05 | 470507 | PE Pipe or Tube | -83 | 0 | 9.48 | 60.6 | 2422.1 | 994.109 | 1048.921 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102620.8 | 45.07 | 103987.9 | PE Pipe or Tube | -79 | 0 | 14.78 | 273.4 | 1367 | 990.423 | 1045.032 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102697.9 | 46.35 | 104142.6 | PE Pipe or Tube | -78 | 0 | 14.77 | 288.9 | 1444.7 | 1019.883 | 1076.116 | 0.4
| On | 0 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 477613.4 | 9.25 | 477613.6 | PE Pipe or Tube | -77 | 0 | 9.45 | 185.2 | 0.2 | 1980.015 | 2089.186 | 0.7
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 555932.8 | 10.29 | 556305.8 | PE Pipe or Tube | -76 | 0 | 9.01 | 74.6 | 373 | 1211.283 | 1278.068 | 0.4
| On | 10 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 563284.5 | 44.95 | 572172.5 | PE Pipe or Tube | -75 | 0 | 8.64 | 888.8 | 8888 | 11475.885 | 12108.623 | 4.1
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 535237.3 | 10.24 | 535594.3 | PE Pipe or Tube | -74 | 0 | 9.11 | 71.4 | 357 | 1161.434 | 1225.471 | 0.4
| On | 30 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 541423.6 | 40.85 | 563409.3 | PE Pipe or Tube | -73 | 0 | 8.72 | 732.9 | 21985.6 | 10264.603 | 10830.554 | 3.7
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102730.4 | 46.87 | 104207.5 | PE Pipe or Tube | -72 | 0 | 14.76 | 295.4 | 1477.2 | 1031.923 | 1088.82 | 0.4
| On | 9 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 482701.9 | 15.53 | 483531.9 | PE Pipe or Tube | -71 | 0 | 9.37 | 92.2 | 830.1 | 3363.063 | 3548.49 | 1.2
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102724 | 46.77 | 104194.9 | PE Pipe or Tube | -70 | 0 | 14.76 | 294.2 | 1470.8 | 1029.588 | 1086.355 | 0.4
| On | 30 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 481382.1 | 10.78 | 482737.7 | PE Pipe or Tube | -69 | 0 | 9.41 | 45.2 | 1355.6 | 2331.14 | 2459.67 | 0.8
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 488393.9 | 10.13 | 488714.6 | PE Pipe or Tube | -68 | 0 | 9.36 | 64.1 | 320.7 | 1048.429 | 1106.236 | 0.4
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 488678.5 | 21.84 | 490962.7 | PE Pipe or Tube | -67 | 0 | 9.27 | 182.7 | 2284.2 | 4800.258 | 5064.926 | 1.7
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 103000 | 51.03 | 104750.4 | PE Pipe or Tube | -66 | 0 | 14.72 | 350.1 | 1750.3 | 1128.049 | 1190.245 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 512803.7 | 38.05 | 527620.9 | PE Pipe or Tube | -65 | 0 | 8.92 | 592.7 | 14817.1 | 8961.971 | 9456.1 | 3.2
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102833.2 | 48.51 | 104413.9 | PE Pipe or Tube | -64 | 0 | 14.75 | 316.1 | 1580.7 | 1069.559 | 1128.53 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 492367.2 | 30.33 | 501298.1 | PE Pipe or Tube | -63 | 0 | 9.13 | 357.2 | 8930.9 | 6797.21 | 7171.983 | 2.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 482019.1 | 10.11 | 482334.9 | PE Pipe or Tube | -62 | 0 | 9.39 | 63.2 | 315.8 | 1033.029 | 1089.987 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 481841.1 | 12.6 | 483372.8 | PE Pipe or Tube | -61 | 0 | 9.39 | 61.3 | 1531.7 | 2728.746 | 2879.198 | 1
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 103281.4 | 55 | 105318.5 | PE Pipe or Tube | -60 | 0 | 14.68 | 407.4 | 2037.1 | 1220.759 | 1288.067 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 546659.7 | 44.45 | 568540.4 | PE Pipe or Tube | -59 | 0 | 8.67 | 875.2 | 21880.7 | 11261.414 | 11882.326 | 4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 502330.6 | 10.17 | 502662.1 | PE Pipe or Tube | -58 | 0 | 9.28 | 66.3 | 331.5 | 1082.075 | 1141.737 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 497440.4 | 30.52 | 506574.8 | PE Pipe or Tube | -57 | 0 | 9.1 | 365.4 | 9134.4 | 6911.106 | 7292.158 | 2.5
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 708090.8 | 142.13 | 839693.6 | PE Pipe or Tube | -56 | 0 | 7.56 | 26320.6 | 131602.8 | 23958.059 | 25279.016 | 8.6
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 582987.2 | 46.99 | 595685.3 | PE Pipe or Tube | -55 | 0 | 8.52 | 1015.9 | 12698.1 | 12482.173 | 13170.393 | 4.5
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 539369.2 | 10.25 | 539729.4 | PE Pipe or Tube | -54 | 0 | 9.09 | 72 | 360.2 | 1171.394 | 1235.981 | 0.4
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 537779.3 | 41.38 | 546781.8 | PE Pipe or Tube | -53 | 0 | 8.8 | 720.2 | 9002.5 | 10090.02 | 10646.345 | 3.6
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 507763.8 | 10.18 | 508099.6 | PE Pipe or Tube | -52 | 0 | 9.25 | 67.1 | 335.7 | 1095.202 | 1155.587 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 501196.3 | 34.33 | 512912 | PE Pipe or Tube | -51 | 0 | 9.03 | 468.6 | 11715.7 | 7866.769 | 8300.513 | 2.8
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 489183.5 | 10.13 | 489504.8 | PE Pipe or Tube | -50 | 0 | 9.35 | 64.3 | 321.3 | 1050.352 | 1108.264 | 0.4
| On | 24 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 486224.7 | 26.08 | 492461.9 | PE Pipe or Tube | -49 | 0 | 9.22 | 259.9 | 6237.2 | 5746.858 | 6063.718 | 2.1
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102748 | 47.16 | 104242.7 | PE Pipe or Tube | -48 | 0 | 14.76 | 299 | 1494.8 | 1038.483 | 1095.741 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 483328.6 | 17.28 | 486181.4 | PE Pipe or Tube | -47 | 0 | 9.34 | 114.1 | 2852.8 | 3761.775 | 3969.185 | 1.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102813.5 | 48.2 | 104373.7 | PE Pipe or Tube | -46 | 0 | 14.75 | 312 | 1560.2 | 1062.419 | 1120.997 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 490875.8 | 26.28 | 497535.5 | PE Pipe or Tube | -45 | 0 | 9.19 | 266.4 | 6659.7 | 5848.687 | 6171.161 | 2.1
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102726.1 | 46.81 | 104199.1 | PE Pipe or Tube | -44 | 0 | 14.76 | 294.6 | 1473 | 1030.399 | 1087.211 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 481251 | 7.86 | 481864.4 | PE Pipe or Tube | -43 | 0 | 9.42 | 24.5 | 613.4 | 1698.347 | 1791.987 | 0.6
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102947.9 | 50.25 | 104644.5 | PE Pipe or Tube | -42 | 0 | 14.73 | 339.3 | 1696.6 | 1109.988 | 1171.189 | 0.4
| On | 12.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 513206.7 | 34.47 | 519143 | PE Pipe or Tube | -41 | 0 | 8.99 | 474.9 | 5936.3 | 7993.181 | 8433.895 | 2.9
| On | 0.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101621.8 | 21.97 | 101644.2 | PE Pipe or Tube | -40 | 0 | 14.9 | 44.7 | 22.3 | 994.109 | 1048.921 | 0.4
| On | 0.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101625 | 22.09 | 101647.6 | PE Pipe or Tube | -39 | 0 | 14.9 | 45.2 | 22.6 | 999.379 | 1054.481 | 0.4
| On | 0.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101619.2 | 21.88 | 101641.4 | PE Pipe or Tube | -38 | 0 | 14.9 | 44.3 | 22.1 | 989.752 | 1044.323 | 0.4
| On | 0.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101614.2 | 21.69 | 101636 | PE Pipe or Tube | -37 | 0 | 14.91 | 43.5 | 21.8 | 981.263 | 1035.366 | 0.4
| On | 1 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 102702.2 | 46.94 | 103011.5 | PE Pipe or Tube | -36 | 0 | 14.81 | 309.3 | 309.3 | 1021.491 | 1077.813 | 0.4
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478566.6 | 6.35 | 478971 | PE Pipe or Tube | -35 | 0 | 9.44 | 16.2 | 404.4 | 1362.303 | 1437.416 | 0.5
| On | 20 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 474728.6 | 17.96 | 477292 | PE Pipe or Tube | -21 | 0 | 9.39 | 128.2 | 2563.4 | 3964.503 | 4183.091 | 1.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 460858.7 | 10.12 | 461160.1 | PE Pipe or Tube | -20 | 0 | 9.54 | 60.3 | 301.4 | 981.263 | 1035.366 | 0.4
| On | 40 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 461263.1 | 10.07 | 463659.9 | PE Pipe or Tube | -19 | 0 | 9.52 | 59.9 | 2396.7 | 981.263 | 1035.366 | 0.4
| On | 5 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 464360.5 | 10.13 | 464664.6 | PE Pipe or Tube | -18 | 0 | 9.52 | 60.8 | 304.1 | 989.752 | 1044.323 | 0.4
| On | 25 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 464662.1 | 19.95 | 470415.6 | PE Pipe or Tube | -17 | 0 | 9.51 | 230.1 | 5753.5 | 1971.015 | 2079.689 | 0.7
| On | 40 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 470548.9 | 9.5 | 471925.1 | PE Pipe or Tube | -16 | 0 | 9.5 | 34.4 | 1376.2 | 1993.488 | 2103.402 | 0.7
| On | 30 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 468328.3 | 10.11 | 470164.9 | PE Pipe or Tube | -15 | 0 | 9.48 | 61.2 | 1836.6 | 999.379 | 1054.481 | 0.4
| On | 2.5 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 470526.1 | 4.75 | 470548.9 | PE Pipe or Tube | -14 | 0 | 9.48 | 9.1 | 22.8 | 994.109 | 1048.921 | 0.4
| On | 30 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 466154.3 | 10.11 | 467980.7 | PE Pipe or Tube | -13 | 0 | 9.5 | 60.9 | 1826.4 | 994.109 | 1048.921 | 0.4
| On | 20 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478204.9 | 6.35 | 478528.7 | PE Pipe or Tube | -12 | 0 | 9.44 | 16.2 | 323.8 | 1362.303 | 1437.416 | 0.5
| On | 140 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478952.6 | 10.96 | 485523.6 | PE Pipe or Tube | -10 | 0 | 9.39 | 46.9 | 6570.9 | 2383.795 | 2515.228 | 0.9
| On | 10 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 465702.1 | 19.99 | 468019.7 | PE Pipe or Tube | -9 | 0 | 9.5 | 231.8 | 2317.6 | 1980.015 | 2089.186 | 0.7
| On | 40 | 89.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 463296 | 10.03 | 465702.2 | PE Pipe or Tube | -8 | 0 | 9.49 | 60.2 | 2406.1 | 989.592 | 1044.154 | 0.4
| On | 40 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 477584.9 | 13.32 | 480532.2 | PE Pipe or Tube | -7 | 0 | 9.4 | 73.7 | 2947.3 | 2999.899 | 3165.302 | 1.1
| On | 10 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 481250.5 | 6.03 | 481398.1 | PE Pipe or Tube | -6 | 0 | 9.42 | 14.8 | 147.6 | 1301.552 | 1373.315 | 0.5
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 574396 | 43.14 | 595985.3 | PE Pipe or Tube | -5 | 0 | 8.55 | 863.6 | 21589.3 | 11475.885 | 12108.623 | 4.1
| On | 10 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 535637 | 37.66 | 541540.3 | PE Pipe or Tube | -4 | 0 | 8.85 | 590.3 | 5903.3 | 9103.169 | 9605.084 | 3.3
| On | 25 | 129.6 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 519034.3 | 38.18 | 534134.6 | PE Pipe or Tube | -1 | 0 | 8.89 | 604 | 15100.3 | 9103.169 | 9605.084 | 3.3
Steel Pipe, Duct or Tube
Unique Name | Status | Length (*) | Inside Diameter (*) | Design Velocity (*) | Design Pressure Gradient (*) | Heat Loss Model | Heat Transfer Coeff (U Value) | Average Soil Temperature (*) | Sizing Pressure Gradient (Pa/m) | Wall Shear Stress (Pa a) | Fluid Shear Rate (in s-1) | Out Stagnation Pressure (Pa a) | In Velocity (m/s) | In Stagnation Pressure (Pa a) | Element Type | User Number | Sizing Velocity (m/s) | Economic Velocity (m/s) | Pressure Gradient (Pa/m) | Friction Loss (Pa) | Flow at NTP (m3/h) | Flow at STP (m3/h) | Flow (kg/s)
| On | 1.875 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478964.6 | 3.97 | 478974.6 | Steel Pipe, Duct or Tube | -144 | 0 | 7.05 | 5.3 | 10 | 1191.889 | 1257.605 | 0.4
| On | 0.625 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478935.8 | 3.97 | 478939.1 | Steel Pipe, Duct or Tube | -143 | 0 | 7.05 | 5.3 | 3.3 | 1191.889 | 1257.605 | 0.4
| On | 0.625 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478952.6 | 3.97 | 478955.9 | Steel Pipe, Duct or Tube | -142 | 0 | 7.05 | 5.3 | 3.3 | 1191.889 | 1257.605 | 0.4
| On | 1.875 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101277.1 | 18.76 | 101325 | Steel Pipe, Duct or Tube | -141 | 0 | 11.4 | 25.5 | 47.9 | 1191.889 | 1257.605 | 0.4
| On | 1 | 102.3 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 489518.8 | 1.68 | 489520.6 | Steel Pipe, Duct or Tube | -137 | 0 | 6.49 | 1.8 | 1.8 | 227.378 | 239.915 | 0.1
| On | 1 | 102.3 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 479381.6 | 8.94 | 479423.1 | Steel Pipe, Duct or Tube | -121 | 0 | 7.05 | 41.5 | 41.5 | 1182.933 | 1248.155 | 0.4
| On | 5 | 102.3 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 479012.9 | 1.72 | 479022.2 | Steel Pipe, Duct or Tube | -111 | 0 | 6.54 | 1.9 | 9.3 | 227.378 | 239.915 | 0.1
| On | 5 | 102.3 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 479130.7 | 8.94 | 479337.6 | Steel Pipe, Duct or Tube | -110 | 0 | 7.05 | 41.4 | 206.9 | 1182.933 | 1248.155 | 0.4
| On | 1 | 102.3 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101316.2 | 8.11 | 101325 | Steel Pipe, Duct or Tube | -90 | 0 | 10.93 | 8.8 | 8.8 | 227.378 | 239.915 | 0.1
| On | 1 | 102.3 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 101112.1 | 42.51 | 101325 | Steel Pipe, Duct or Tube | -89 | 0 | 11.4 | 212.9 | 212.9 | 1182.933 | 1248.155 | 0.4
| On | 10 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 479007.3 | 0.76 | 479009.8 | Steel Pipe, Duct or Tube | -32 | 0 | 6.54 | 0.3 | 2.5 | 227.378 | 239.915 | 0.1
| On | 5 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478935.8 | 4.53 | 478970.3 | Steel Pipe, Duct or Tube | -29 | 0 | 7.09 | 6.9 | 34.5 | 1410.311 | 1488.07 | 0.5
| On | 18 | 154.1 | 1.15 | 360 | Ignore Heat Loss/Gain | Calculate U Value | 15 | 0 | 0 | 0 | 478243.5 | 8.36 | 478662.7 | Steel Pipe, Duct or Tube | -22 | 0 | 7.18 | 23.3 | 419.2 | 2602.199 | 2745.675 | 0.9
Bend
Unique Name | Status | Elevation (*) | User Number | Flow (kg/s) | Friction Loss (Pa) | Element Type | In Stagnation Pressure (Pa a) | Out Stagnation Pressure (Pa a)
| On | 0 | 1 | 3.3 | 1502.2 | Bend | 535636.9 | 534134.7
| On | 0 | 5 | 4.1 | 2222.8 | Bend | 574395.4 | 572172.6
| On | 0 | 7 | 0.7 | 409.1 | Bend | 468428.8 | 468019.7
| On | 0 | 10 | 0.5 | 37.9 | Bend | 478566.6 | 478528.7
| On | 0 | 12 | 0.4 | 104.3 | Bend | 468085 | 467980.7
| On | 0 | 19 | 0.4 | 103.1 | Bend | 461263.2 | 461160.1
| On | 0 | 31 | 0.1 | 3.2 | Bend | 479012.9 | 479009.8
| On | 0 | 150 | 0.4 | 13.4 | Bend | 478952.6 | 478939.1
T Junction
Unique Name | Status | Elevation (*) | Branch Loss (Pa) | Temperature (C) | Channel Stagnation Pressure (Pa a) | Straight Loss (Pa) | Straight K (based on channel flow) | Straight Flow (kg/s) | User Number | Branch K (based on channel flow) | Branch Flow (kg/s) | Friction Loss (Pa) | Channel Flow (kg/s) | Element Type
| On | 0 | 0 | 13.2 | 480532.2 | 0 | 0 | 0 | 2 | 0 | 1.1 | 0 | 1.1 | T Junction
| On | 0 | 1800 | 13.2 | 485559.8 | 36.2 | 0.0175 | 0.9 | 6 | 0.8711 | 1.2 | 0 | 2.1 | T Junction
| On | 0 | 1001.5 | 13.1 | 465702.2 | 0 | 0 | 0.4 | 8 | 0.875 | 0.4 | 0 | 0.7 | T Junction
| On | 0 | 384.1 | 15.3 | 470548.9 | 0.1 | 0.0002 | 0.4 | 15 | 1.4858 | 0.4 | 0 | 0.7 | T Junction
| On | 0 | 1506.7 | 15.3 | 471922.3 | -2.9 | -0.0028 | 0.7 | 16 | 1.4781 | 0.7 | 0 | 1.4 | T Junction
| On | 0 | 1002.3 | 15.3 | 464662.2 | -2.4 | -0.0021 | 0.4 | 18 | 0.8751 | 0.4 | 0 | 0.7 | T Junction
| On | 0 | 665.2 | 15.4 | 477292 | 566.5 | 0.5618 | 0.5 | 21 | 0.6597 | 0.9 | 0 | 1.4 | T Junction
| On | 0 | 0 | 16.6 | 478662.7 | 0 | 0.5242 | 0 | 28 | 0.4088 | 0.9 | 0 | 0.9 | T Junction
| On | 0 | 160.4 | 16.5 | 478970.3 | 37 | 0.5791 | 0.1 | 33 | 2.5122 | 0.4 | 0 | 0.5 | T Junction
| On | 0 | 487.8 | 13.1 | 478953 | -18 | -0.05 | 0.5 | 39 | 1.3535 | 0.4 | 0 | 0.9 | T Junction
| On | 0 | 4795.6 | 13.3 | 519033.9 | -109.1 | -0.0225 | 2.9 | 45 | 0.9885 | 0.4 | 0 | 3.3 | T Junction
| On | 0 | 594.7 | 13.2 | 481840.9 | -23.5 | -0.05 | 0.6 | 47 | 1.2671 | 0.4 | 0 | 1 | T Junction
| On | 0 | 2928 | 13.2 | 497440 | -95.5 | -0.0327 | 2.1 | 49 | 1.0038 | 0.4 | 0 | 2.5 | T Junction
| On | 0 | 1515.4 | 13.2 | 486109.4 | -72 | -0.05 | 1.4 | 51 | 1.0525 | 0.4 | 0 | 1.7 | T Junction
| On | 0 | 2863.1 | 13.2 | 492367.9 | -94.1 | -0.033 | 2.1 | 53 | 1.0043 | 0.4 | 0 | 2.4 | T Junction
| On | 0 | 4705.1 | 13.3 | 512804.6 | -107.4 | -0.0226 | 2.8 | 55 | 0.9886 | 0.4 | 0 | 3.2 | T Junction
| On | 0 | 6931.7 | 13.4 | 546660.9 | -120.8 | -0.0171 | 3.6 | 57 | 0.983 | 0.4 | 0 | 4 | T Junction
| On | 0 | 0 | 13.7 | 708096.4 | 0 | 0 | 0 | 59 | 3.0119 | 8.6 | 0 | 8.6 | T Junction
| On | 0 | 3810.2 | 13.3 | 506472.3 | -102.4 | -0.0267 | 2.5 | 61 | 0.9941 | 0.4 | 0 | 2.9 | T Junction
| On | 0 | 8167.4 | 13.5 | 568412 | -128.4 | -0.0154 | 4 | 63 | 0.9817 | 0.4 | 0 | 4.5 | T Junction
| On | 0 | 993.5 | 13.2 | 483328.4 | -44.5 | -0.05 | 1 | 65 | 1.1172 | 0.4 | 0 | 1.4 | T Junction
| On | 0 | 3730.7 | 13.2 | 501197.1 | -101 | -0.0269 | 2.4 | 67 | 0.9944 | 0.4 | 0 | 2.8 | T Junction
| On | 0 | 5778.2 | 13.4 | 527507 | -113.8 | -0.0194 | 3.2 | 69 | 0.9851 | 0.4 | 0 | 3.6 | T Junction
| On | 0 | 2160.9 | 13.2 | 490875.5 | -87.3 | -0.0412 | 1.7 | 71 | 1.0208 | 0.4 | 0 | 2.1 | T Junction
| On | 0 | 472.2 | 13.2 | 481382.5 | -15.6 | -0.0455 | 0.5 | 73 | 1.3767 | 0.4 | 0 | 0.8 | T Junction
| On | 0 | 825.6 | 13.2 | 482702.1 | -35.6 | -0.05 | 0.8 | 75 | 1.1597 | 0.4 | 0 | 1.2 | T Junction
| On | 0 | 5828.6 | 13.4 | 541423.1 | -117.2 | -0.0198 | 3.3 | 77 | 0.9855 | 0.4 | 0 | 3.7 | T Junction
| On | 0 | 6977.9 | 13.5 | 563284.2 | -125.1 | -0.0176 | 3.7 | 79 | 0.9834 | 0.4 | 0 | 4.1 | T Junction
| On | 0 | 691.4 | 13.1 | 477585 | -28.6 | -0.05 | 0.7 | 81 | 1.2078 | 0.4 | 0 | 1.1 | T Junction
Open Pipe Boundary
Unique Name | Status | Elevation (*) | User Number | Flow (kg/s) | Solids Delivered (kg/s) | Friction Loss (Pa) | Element Type | In Stagnation Pressure (Pa a) | Out Stagnation Pressure (Pa a)
| On | 0 | 9 | 0.4 | 0 | 1294 | Open Pipe Boundary | 102618.9 | 101325
| On | 0 | 13 | 0.4 | 0 | 296.8 | Open Pipe Boundary | 101621.8 | 101325
| On | 0 | 14 | 0.4 | 0 | 300 | Open Pipe Boundary | 101625 | 101325
| On | 0 | 17 | 0.4 | 0 | 294.3 | Open Pipe Boundary | 101619.2 | 101325
| On | 0 | 20 | 0.4 | 0 | 289.2 | Open Pipe Boundary | 101614.2 | 101325
| On | 0 | 40 | 0.4 | 0 | 1377.6 | Open Pipe Boundary | 102702.5 | 101325
PIT 01 | On | 0 | 46 | 0.4 | 0 | 1622.8 | Open Pipe Boundary | 102947.8 | 101325
PIT 15 | On | 0 | 48 | 0.4 | 0 | 1401.4 | Open Pipe Boundary | 102726.4 | 101325
PIT 07 | On | 0 | 50 | 0.4 | 0 | 1488.6 | Open Pipe Boundary | 102813.6 | 101325
PIT 11 | On | 0 | 52 | 0.4 | 0 | 1423.2 | Open Pipe Boundary | 102748.2 | 101325
| On | 0 | 54 | 0.4 | 0 | 1455.4 | Open Pipe Boundary | 102780.4 | 101325
| On | 0 | 56 | 0.4 | 0 | 1580.5 | Open Pipe Boundary | 102905.5 | 101325
| On | 0 | 58 | 0.4 | 0 | 1804.3 | Open Pipe Boundary | 103129.2 | 101325
PIT 05 | On | 0 | 62 | 0.4 | 0 | 1543.4 | Open Pipe Boundary | 102868.4 | 101325
PIT 06 | On | 0 | 64 | 0.4 | 0 | 1956.7 | Open Pipe Boundary | 103281.6 | 101325
PIT 13 | On | 0 | 66 | 0.4 | 0 | 1408.5 | Open Pipe Boundary | 102733.5 | 101325
PIT 14 | On | 0 | 68 | 0.4 | 0 | 1508.4 | Open Pipe Boundary | 102833.4 | 101325
PIT 10 | On | 0 | 70 | 0.4 | 0 | 1675.2 | Open Pipe Boundary | 103000.2 | 101325
PIT 09 | On | 0 | 72 | 0.4 | 0 | 1450.2 | Open Pipe Boundary | 102775.2 | 101325
PIT 17 | On | 0 | 74 | 0.4 | 0 | 1399.2 | Open Pipe Boundary | 102724.2 | 101325
PIT 18 | On | 0 | 76 | 0.4 | 0 | 1405.5 | Open Pipe Boundary | 102730.5 | 101325
PIT 02 | On | 0 | 78 | 0.4 | 0 | 1774.1 | Open Pipe Boundary | 103099.2 | 101325.1
PIT 03 | On | 0 | 80 | 0.4 | 0 | 1926.8 | Open Pipe Boundary | 103251.9 | 101325.1
PIT 19 | On | 0 | 82 | 0.4 | 0 | 1373.4 | Open Pipe Boundary | 102698.3 | 101325
PIT 21 | On | 0 | 83 | 0.4 | 0 | 1296.1 | Open Pipe Boundary | 102621.1 | 101325
Butterfly Valve
Unique Name | Status | Elevation (*) | User Number | Flow (kg/s) | Friction Loss (Pa) | Element Type | In Stagnation Pressure (Pa a) | Out Stagnation Pressure (Pa a)
| On | 0 | 41 | 0.4 | 359233.7 | Butterfly Valve | 460858.7 | 101625
| On | 0 | 42 | 0.4 | 362729.4 | Butterfly Valve | 464360.5 | 101631.1
| On | 0 | 43 | 0.4 | 366690.4 | Butterfly Valve | 468328.3 | 101637.9
| On | 0 | 44 | 0.4 | 364520.6 | Butterfly Valve | 466154.4 | 101633.8
| On | 0 | 95 | 8.6 | 17373.6 | Butterfly Valve | 857066.9 | 839693.3
| On | 0 | 96 | 0.4 | 434369.4 | Butterfly Valve | 539369.2 | 104999.8
| On | 0 | 97 | 0.4 | 403211 | Butterfly Valve | 507763.8 | 104552.8
| On | 0 | 98 | 0.4 | 450644.3 | Butterfly Valve | 555932.8 | 105288.5
| On | 0 | 99 | 0.4 | 454560.8 | Butterfly Valve | 559868.8 | 105308
| On | 0 | 100 | 0.4 | 416638.9 | Butterfly Valve | 521382.7 | 104743.7
| On | 0 | 101 | 0.4 | 392731.5 | Butterfly Valve | 497138.9 | 104407.5
| On | 0 | 102 | 0.4 | 384882.1 | Butterfly Valve | 489183.5 | 104301.4
| On | 0 | 103 | 0.4 | 377358 | Butterfly Valve | 481561.2 | 104203.2
| On | 0 | 104 | 0.4 | 373596 | Butterfly Valve | 476597.5 | 103001.5
| On | 0 | 105 | 0.4 | 372450.7 | Butterfly Valve | 476582.1 | 104131.4
| On | 0 | 106 | 0.4 | 376743.2 | Butterfly Valve | 480931.3 | 104188.1
| On | 0 | 107 | 0.4 | 380042.3 | Butterfly Valve | 484276.5 | 104234.3
| On | 0 | 109 | 0.4 | 377815.9 | Butterfly Valve | 482019.1 | 104203.2
| On | 0 | 110 | 0.4 | 376407.7 | Butterfly Valve | 480595.6 | 104188
| On | 0 | 111 | 0.4 | 389817.4 | Butterfly Valve | 494186.8 | 104369.5
| On | 0 | 112 | 0.4 | 360672 | Butterfly Valve | 463296.1 | 102624.1
| On | 0 | 113 | 0.4 | 360423.5 | Butterfly Valve | 464398.7 | 103975.2
| On | 0 | 115 | 0.4 | 44 | Butterfly Valve | 479381.6 | 479337.6
| On | 0 | 116 | 0.1 | 10496.6 | Butterfly Valve | 489518.8 | 479022.2
| On | 0 | 117 | 0.4 | 397845.8 | Butterfly Valve | 502330.6 | 104484.8
| On | 0 | 118 | 0.4 | 409249.8 | Butterfly Valve | 513897.8 | 104648
| On | 0 | 119 | 0.4 | 430273.3 | Butterfly Valve | 535237.3 | 104964
| On | 0 | 122 | 2.1 | 392.7 | Butterfly Valve | 486225.2 | 485832.6
| On | 0 | 123 | 1.2 | 135.2 | Butterfly Valve | 483667.1 | 483531.9
| On | 0 | 124 | 0.4 | 384105.1 | Butterfly Valve | 488393.9 | 104288.8
| On | 0 | 149 | 0.4 | 8.7 | Butterfly Valve | 478964.6 | 478955.9
| On | 0 | 153 | 2.9 | 719.7 | Butterfly Valve | 513206.6 | 512486.9
| On | 0 | 154 | 1.7 | 272.5 | Butterfly Valve | 488678.4 | 488405.8
| On | 0 | 155 | 4.5 | 1543.7 | Butterfly Valve | 582987.9 | 581444.2
| On | 0 | 156 | 3.6 | 1094.8 | Butterfly Valve | 537779.7 | 536684.8
| On | 0 | 157 | 1.4 | 192.8 | Butterfly Valve | 474728.7 | 474535.8
| On | 0 | 158 | 0.5 | 22.4 | Butterfly Valve | 478204.9 | 478182.4
Diffuser/Reducer
Unique Name | Status | Elevation (*) | Reducer Type | Reducer Length (*) | User Number | Flow (kg/s) | Friction Loss (Pa) | Element Type | In Stagnation Pressure (Pa a) | Out Stagnation Pressure (Pa a)
| On | 0 | Concentric | 0.2 | 87 | 0.4 | 19.1 | Diffuser/Reducer | 470526.1 | 470507
| On | 0 | Concentric | 0.2 | 88 | 0.7 | 74.1 | Diffuser/Reducer | 477613.4 | 477539.3
Connector
Unique Name | Status | Elevation (*) | User Number | Stagnation Pressure (Pa a) | Temperature (C)
| On | 0 | 89 | 478243.5 | 16.6
Positive Displacement Compressor
Unique Name | Status | Elevation (*) | User Number | Duty Flow (kg/s) | Duty Pressure Rise (Pa) | Duty NPSH Available (m Fluid) | Element Type | In Stagnation Pressure (Pa a) | Out Stagnation Pressure (Pa a)
| On | 0 | 126 | 0.4 | 378311 | 0 | Positive Displacement Compressor | 101112.1 | 479423.1
| On | 0 | 140 | 0.1 | 388204.4 | 0 | Positive Displacement Compressor | 101316.2 | 489520.6
| On | 0 | 151 | 0.4 | 377697.5 | 0 | Positive Displacement Compressor | 101277.1 | 478974.6
Known Pressure Boundary
Unique Name | Status | Elevation (*) | Temperature (*) | Pressure (*) | Fluid | User Number | Element Type | Flow (kg/s) | Solids Delivered (kg/s) | Density (kg/m3) | Viscosity (cP)
| On | 0 | 15 | 1 | air | 146 | Known Pressure Boundary | 0.4 | 0 | 1.2 | 0.017895
| On | 0 | 15 | 1 | air | 147 | Known Pressure Boundary | 0.4 | 0 | 1.2 | 0.017895
| On | 0 | 15 | 1 | air | 148 | Known Pressure Boundary | 0.1 | 0 | 1.2 | 0.017895
| On | 0 | 15 | 8.6 | air | 152 | Known Pressure Boundary | 8.6 | 0 | 11.7 | 0.017895

## Bill Of Materials
Bill Of Materials
Nodes
Bend - Idelchik | 8
Tee Junction - Idelchik | 29
Open Pipe | 25
Butterfly Valve - Generic Butterfly Valve - Miller Data | 37
Reducer / Expander | 2
Connector (No Resistance) | 1
Positive Displacement Pump or Compressor - L132 | 3
Known or Assigned Pressure | 4
Pipes
Polyethylene (PE) Pipe or Duct - 160 mm - SDR11/PN12.5 | 834.50 m
Steel Pipe or Duct - 6 inch - Schedule 40 | 38.00 m
Steel Pipe or Duct - 4 inch - Schedule 40 | 14.00 m
Polyethylene (PE) Pipe or Duct - 110 mm - SDR11/PN12.5 | 496.00 m