## Sheet1
Calculation of Actual Contaminated Firewater Volume
In the analysis of fire accidents in process plants, the main attention is usually given to the damages caused by
fire to personnel, equipment and structures, while the environmental issues due to contamination by means
of polluted firewater are often underestimated, even though they can also lead to severe consequences.
A proper design of waste water retention and treatment systems can cope with these issues and the key factor
to be evaluated in the design of such system is the actual amount of contaminated firewater to be collected,
contained and treated.
The estimation of actual contaminated firewater volume is based on the following equation, generally applicable
to all the considered fire scenarios.
where:
VFW = | Actual contaminated firewater volume, m3
QFW = | Firewater flow rate, m3/h
Note: It is assumed for each scenario that the same amount of required firewater flow rate, that may be given by a combination of manual and automatic fire fighting systems, is continuously used to fight the fire from the beginning till fire is completely stopped.
tf = | Fire scenario duration, hrs
K = | Reduction factor, which takes into account effects like evaporation of water in contact with fire & high
temperature surfaces, as well as dispersion of water onto unpaved areas, especially by wind effect.
Note: A maximum value of 0.9 is recommended for 'K'
Duration of Fire Scenario
where:
tf = | Fire scenario duration, hrs
h = | height of liquid pool, m
vb = | burning rate, m/s
where:
V = | volume of liquid pool, m3
g = | acceleration due to gravity, "9.81" m/s2
Scenario 1: Flammable Liquid Fire
Table for "Burning Rates" vb for Flammable Liquids
Liquid | Mass Burning Rate, m, kg/m2.sec | Density, kg/m3 | Burning Rate, m/s
Benzene | 0.085 | 874 | 9.7254e-05
Hexane | 0.074 | 650 | 0.00011385
Heptane | 0.101 | 675 | 0.00014963
Xylene | 0.09 | 870 | 0.00010345
Benzine | 0.048 | 740 | 6.4865e-05
Gasoline | 0.055 | 740 | 7.4324e-05
Kerosene | 0.039 | 820 | 4.7561e-05
Scenario 2: Combustible Liquid Fire
Table for "Burning Rates" vb for Combustible Liquids
Liquid | Mass Burning Rate, m, kg/m2.sec | Density, kg/m3 | Burning Rate, m/s
Diesel | 0.045 | 918 | 4.902e-05
Transformer oil | 0.039 | 760 | 5.1316e-05
Heptane | 0.101 | 675 | 0.00014963
Fuel Oil | 0.035 | 970 | 3.6082e-05
Crude Oil | 0.034 | 855 | 3.9766e-05
Lube Oil | 0.039 | 760 | 5.1316e-05
Note:
For systems handling combustible liquids, height of liquid pool may be calculated alternatively as "V/A," where A is the area
inside the curb, since they are generally stored in tanks located in curbed areas.
Inputs
Liquid Spill Quantity = | 11340 | kg
Liquid Type = | Gasoline
Density = | 740 | kg/m3
Burning Rate, vb = | 7.4324e-05 | m/s
QFW = | 454 | m3/h
K = | 0.9 | dimensionless
Outputs
Vol. of Liquid pool, V = | 15.3243 | m3
h = | 0.0055278 | m
tf = | 0.020659 | hrs
VFW = | 8.4414 | m3
Reference
Actual Firewater Consumption
Prepared by: | Ankur Srivastava
Chemical Engineer
Email: | ankur_2061@hotmail.com
E