## Theory
Objective:
This excel sheet provides the calculation basis and sample calculation for identifying how much steam can be lost due to malfunctioning steam traps.
Lt,y = (1/2.2046) . FTt,y . FSt,y . CVt,y . ht,y .((Pin,t - Pout,t).(Pin,t + Pout,t))0.5 |  |  |  |  | (Equation 1)
Lt,y | kg/year | Loss of steam due to malfunctioning steam trap
FTt,y |  | Failure type factor of steam trap
FSt,y |  | Service factor of steam trap
CVt,y |  | Flow coefficient of steam trap
ht,y | hrs | number of hours of steam trap operation
Pin,t | psia | Steam pressure upstream of steam trap
Pout,t | psia | Steam pressure downstream of steam trap
Equation 1 is applicable in malfunctioning steam traps (blow-through, leaking, rapid cycling) for Pout,t ≥ Pin,t/2
Lt,y = (1/2.2046) . FTt,y . FSt,y . CVt,y . ht,y .((Pin,t - Pin,t / 2).(Pin,t + Pin,t / 2))0.5 |  |  |  |  | (Equation 2)
Equation 2 is applicable in malfunctioning steam traps (blow-through, leaking, rapid cycling) for Pout,t < Pin,t/2
Table 1: Failure type factor FT
Type of failure |  | FT
Blow through (BT) |  | 1
Leaking (LK) |  | 0.25
Rapid cycling (RC) |  | 0.2
FS = 2.1 * (1 - 1/ S)
S | Capacity safety factor (ratio between trap capacity (orifice) and the actual condensate load)
Table 2: Service Factor FS
Application |  |  | FS | S
Process steam traps |  |  | 0.9 | 1.75
Drip and tracer steam traps |  |  | 1.4 | 3
Steam flow (no condensate) |  |  | 2.1 | Very large
CV = 22.1 D2
D | inch | Orifice diameter of steam trap
Ref.: | http://cdm.unfccc.int/EB/020/eb20repan10.pdf

## Calculation
Sample calculation is given below:
Input parameters:
D | 0.078125 | inch | Orifice diameter of steam trap
Type of failure | Blow through (BT)
FT | 1 |  | Failure type factor of steam trap
Application | Steam flow (no condensate)
FS | 2.1 |  | Service factor of steam trap
CV | 0.13489 |  | Flow coefficient of steam trap
ht,y | 8760 | hrs | number of hours of steam trap operation per annum
Pin,t | 638.1921 | psia | Steam pressure upstream of steam trap
Pout,t | 174.1921 | psia | Steam pressure downstream of steam trap
Is Pout,t ≥ Pin,t/2 ? | No
Lt,y | 622082.5295 | kg/year | Loss of steam due to malfunctioning steam trap
Lt,y | 71.014 | kg/h | Loss of steam due to malfunctioning steam trap
Lt,y | 156.4874 | lb/h | Loss of steam due to malfunctioning steam trap
Unit cost of steam | 5 | USD / ton
Annual steam cost | 3110.4126 | USD | Annual cost of steam due to malfunctioning steam trap
Prepared by:
Ajay S. Satpute
Sr. Process Engineer
M. Tech. (Chemical)
I.I.T., Madras, INDIA
Ramboll Consulting Engineering, Qatar
Note on A3: Only the YELLOW boxes may be changed.