## Instruction Sheet
INSTRUCTION FOR FILLING UP THE FORM-Sh
Sr No | Details | Basis/Formule | Note | Frequency | Primary Documents from where the information can be sourced and to be kept ready for verification by Accredited Energy Auditor | Secondary Documents from where the information can be sourced and to be kept ready for verification by Accredited Energy Auditor
It is mandatory to fill all the fields of Excel sheets-General Information sheet and Form Sh, For Baseline Year data Entry: DC to provide average data for three years 2007-08, 2008-09 and 2009-10 , if otherwise specified
Please fill the data as per colour coding provided at the bottom of Form Sh
The DC may submit separate Excel sheet for additional information required for Heat Rate calculation or Normalisation for different module combination or load
1 | Please provide the name of unit /Station | To be filled in the General Information Sheet
2 | Please provide the year of establishment of the Station | To be filled in the General Information Sheet
3 | Please provide the type of the Station | To be filled in the General Information Sheet. .
4 | Plant Details
i | Please provide the total MW installed Capacity of the Station | To be filled in the Form-Sh Sheet directly | 1. Form Sh is to be filled for Gas/Oil Fired Thermal Power plant also, however the Normalisation for Fuel Mix will be dealt separately. 2. The other calculation will be performed based on the mearit of the parameters in Form Sb | One time | COD document | PPA
ii | Please provide unit configuration (i.e. 3x100 + 2x250 + 2x500+ ------- etc.) of the Station | To be filled in the Form-Sh Sheet directly |  | One time | COD document | PPA
iii | Notified Baseline Net Heat Rate (kcal/kWh) |  |  | One time | Notification S.O. 387 (E ) | Calculation for target setting
iv | Notified Target Net Heat Rate (kcal/kWh) |  |  | One time | Notification | Calculation for target setting
v | Notified Net Product output (Net Generation) in Million Units |  |  | One time | Notification | Calculation for target setting
vi | % Reduction Target for Percentage deviation in the Station Net Heat Rate as per Notificataion | Shall be calculated as per the formula given in the PAT documents |  | One time | Notification | Calculation for target setting
5 | Unit wise Design Data Details
5 | Please provide the Unitwise design installed Capacity, Boiler Efficiency, Turbine Heat rate and Unit Heat rate provided by Original Equipment Manaufacturer (OEM) and as per Performance Guarantee Test (PG Test) report and the Commercial Operation Date (COD) of all the Unit. The data to be provided for Major Fuel | Unit Design Heat Rate (UDHR) = Turbine Heat Rate /Boiler Efficiency, & COD in terms of Date format xx/xx/xxxx |  | One time | 1. OEM Curves and docuemts/ COD documents 2 PG Test Report 3. HMB diagram at different load (Minimum 5-7 nos of (x,y) co-ordinates to plot as curve 4. Design Boiler Efficiency Document from Original Equipment Manufacturer (OEM) 5. Design Coal Analysis Document as per OEM 6. Predicted Performance Data (PPD) document from OEM | 1.Plant Design document from OEM 2. PG Test Report
5.1 | Calculation for Station installed Capacity, Boiler Efficiency, Turbine Heat rate and Unit Heat rate provided by Original Equipment Manaufacturer (OEM) and as per Performance Guarantee Test (PG Test) report and the commercial operation date (COD) of all the Unit. | Station's Design Heat Rate = [UDHR1xC1 + UDHR2xC2+ UDHR3xC3………]/[C1+C2+C3…….] Where C1, C2, C3, …..= Unit Capacity in MW |  | One time
5.2 | Please provide the Unitwise design installed Capacity, Boiler Efficiency, Turbine Heat rate and Unit Heat rate provided by Original Equipment Manaufacturer (OEM) and as per Performance Guarantee Test (PG Test) report and the Commercial Operation Date (COD) of all the Unit. The data to be provided for Other Fuel |  |  | One time | 1. OEM Curves and docuemts/ COD documents 2 PG Test Report 3. HMB diagram at different load (Minimum 5-7 nos of (x,y) co-ordinates to plot as curve 4. Design Boiler Efficiency Document from Original Equipment Manufacturer (OEM) 5. Design Coal Analysis Document as per OEM | 1.Plant Design document from OEM 2. PG Test Report
6 | Unit wise Operating Data Details
6.a | Please provide the Unitwise Operating details such as Operating Load, Unit Load factor, Gross Generation, Unit Heat rate for the present year as well as for the previous year | To be filled in the Form-Sh Sheet directly |  | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6) Internal Audit Report 7) Efficiecny Report
6.b | Please provide the Station's Operating details such as Operating Load, Plant Load factor, Gross Generation, Station Heat rate for the present year as well as for the previous year. | Station Operating Gross Heat Rate = [(OGHR 1 x Generation 1 + OGHR 2 x Generation 2 + -----------) / (Total Generation of Station)] |  | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6) Internal Audit Report
7 | Station's Generation & PLF details/ Other Details |  |  | Primary-Annual Secondary-Daily reports | Annual Generation Reports | Daily Generation Reports
| Plant Details | as per Sr No 4 (i)
i | Please provide installed capacity (MW) of the station for current as well as for the previous year | if the COD of a 200 MW unit is 1st October, its weighted capacity for the whole year is |  |  | 1. OEM Document
ii | If COD of some unit(s) is in between the year, Please provide the total station's weighted capacity for the year in MW | For example : if the COD of a 200 MW unit is 1st October in the current year, its weighted capacity for the whole year is 100 MW |  |  | 1. COD Document submitted to Authority
iii | Please provide total Gross Generation (MU) of the station for current as well as for previous year | Total Gross Generation = Gen1 + Gen2 +Gen3+……… |  | Primary-Annual Secondary-Daily reports | 1. Annual Generation Reports 2. DGR 3. MGR 4. Annual Report | 1. Energy Management System 2. Energy Meters
iv | Calculation of Plant Availability Factor (%) | The calculation is to be done from Planned or unplanned staoppages, Forced outage etc of unit |  | Daily, Monthly, Annual | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Generation Schedule from Load Despatch Centre 5) External Breakdown Report 6) Fuel Unavailability document/record from external agencies 7) Coal Linkage Document 8) Log Book | 1) Shift Register 2) Shift Reports 3) Energy Meter Readings 4) Energy Management System 5) Breakdown reports (Internal and External)
v | Please provide total Plant Load factor (%) of the station for current as well as for previous year | Plant Load Factor (%) = Gross generation (MU)/(Installed Capacity (MW) X 8.76) | Example-For Calculating ULF of the unit commissioned during the year : if the COD of a 200 MW unit is 1st October and PLF for the remaining period is 80% , its weighted capacity for the whole year is 100 MW, with weighted for whole year PLF stands at 40% | Primary-Annual Secondary-Daily reports | 1. Annual Generation Reports 2. DGR 3. MGR 4. Annual Report | 1. Energy Management System 2. Energy Meters
vi | Reference from other cell: Auxiliary Power Consumption (APC) in MU | APC = Gross Genration - Generation send out to grid | The Auxilliary Power of the Station to be provided without Colony and construction power | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
vii | Calculation of Auxiliary Power Consumption (APC) in %
viii | Calculation of operating gross heat rate of the station | same as calculated in row no. 6.b |  | Primary -Daily Secondary- Daily | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6. Efficiency Report
ix | Calculation of operating Net heat rate (ONHR) of the station. | ONHR = OGHR/(1-APC/100) |  | Primary -Daily Secondary- Daily | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6. Efficiency Report
x | Please provide the Average PLF during Baseline year as per baseline energy audit reports |  |  |  | 1) baseline Report
xi | Please provide Actual PLF as reported to CERC/SERC |  |  |  | 1) Reporting document to CERC/SERC
xii | Please provide the Operation Norms for Thermal Power Stations Gross Heat rate Tariff Period - 2014 - 19 as per CERC/SERC |  |  |  | 1)Tariff Document from CERC
xiii | Reference from other Cell: Station Net Operating Heat Rate as per Notification (Baseline)
xiv | Reference from other Cell: Station Net Target Heat Rate as per Notification (Baseline)
7.1 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii) in case of Gas based Power Station or Thermal Oil-Gas based Plant)
a | Please provide the Annual Genertion for Actual Gross Generation-Closed Cycle in differnet type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  | DC to provide the details of generation through Gas or Oil field for Gas or Oil based Thermal Power Plant | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Fuel Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Fuel Flow Meter 4) Gas Meter 5) Fuel GCV test report (Internal and External) 6. Efficiency Report 7. GCV/NCV test report from external or internal test report
b | Please provide the Annual Genertion in MU for Actual Gross Generation-Open Cycle due to Internal factor in differnet type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  | DC to provide the details of generation through Gas or Oil field for Gas or Oil based Thermal Power Plant | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Fuel Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Fuel Flow Meter 4) Gas Meter 5) Fuel GCV test report (Internal and External) 6. Efficiency Report 7. GCV/NCV test report from external or internal test report
c | Please provide the Annual Genertion in MU for Actual Gross Generation-Open Cycle due to External factor in differnet type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  | DC to provide the details of generation through Gas or Oil field for Gas or Oil based Thermal Power Plant | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Fuel Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Fuel Flow Meter 4) Gas Meter 5) Fuel GCV test report (Internal and External) 6. Efficiency Report 7. GCV/NCV test report from external or internal test report
7.2 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii), 7(vi) in case of Gas based Power Station)
i | Please provide the Auxiliary Power Consumption in MU for different type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  |  | Primary-Annual Secondary-Hourly shift log book/ Daily reports | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
ii | Reference from other Cell:Actual Gross Generation-Closed Cycle
iii | Reference from other Cell:Actual Gross Generation -Open Cycle due to internal factor
iv | Reference from other Cell:Actual Gross Generation-Open Cycle due to external factor
v | Reference from other Cell:Actual Gross Generation
vi | calculation: Auxiliary Power Consumption
8 | Details of Electricity Purchased from the Grid (MUs)
i | Please provide the purchased electricity if any. |  |  |  | 1) Grid Meter report 2) Daily Power Report 3) DGR 4) MGR | 1) Meter Reading 2) Energy management System
ii | Please provide the reason if plant has purchased electricity |  |  |  | Basis Report
9 | Details of Electricity Generated
i | Reference from other Cell:Total Gross Generation of Electricity | To be filled in the Form-Sh Sheet directly |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
ii | Reference from other Cell:Total Net Electricity Supplied to Grid | Total Supplied to grid =Total Generation -APC |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
iii | Please provide Electricity Consumption-Colony/Construction | To be filled in the Form-Sh Sheet directly |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
iv | Total Electricity used inhouse for Power Generation i.e. APC (Without colony, construction & others consumption) |  |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
v | Any other (specify) | To be filled in the Form-Sh Sheet directly |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
10 | Unitwise Fuel Analysis Details (As Fired Basis)
10. 1. | Please provide the Unitwise Solid Fuel's (Coal/Lignite Fuel) Proximate and Ultimate Analysis details in row 10.1 A to 10.1.J for design fuel, PG test fuel, current year and as well for previous year fuel used for Electricity Production/Generation. |  |  | Primary-daily secondary- every 4 hours | 1) Daily Internal Report from Lab on Fuel Proximate Analysis performed on each lot. 2) Test Certificate from Government Accredited lab. (Plant to maintain minimum 1 sample test in a quarter for Proximate and Ultimate Analysis i.e. 4 test certificates in a year for each soild fuel 3) Purchase Order, where guaranteed GCV range is mentioned | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document
a | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant | Energy Consumption to be entered in Form Sh |  | Primary-daily secondary- every 4 hours | DGR | Energy Meter Reports
10. 2. | Please provide the Gas fuel Analysis for design fuel, PG test fuel, Current year and as well for Previous year fuel used for Electricity Production/Generation. | Conversion factor from GCV to NCV in the baseline year shall be 1.1 or as submitted by the Gas suppler |  | Primary-daily secondary- every 4 hours | 1) Test report from Supplier 2) Lab analysis report for samples at various points | FSA, Lab analysis report for samples at various points
11 | Details of Fuel Consumption as fired basis
11.1 | Please provide the Gross Calorific Value, Total Consumption and Specific Fuel Consumption of Solid Fuels (Coal/Lignite/others) as fired basis | Specific Fuel Consumption = Quantity of Fuel Energy input to Plant X Gross GCV of Fuel/ output generated from palnt | Landed cost of Fuel is required to calculate the price of 1 ESCerts for the year 2014-15. | Primary-daily/ shift wise secondary- every 4 hours | 1) Daily Internal Report from Lab on Fuel Proximate Analysis performed on each lot. 2) Test Certificate from Government Accredited lab. (Plant to maintain minimum 1 sample test in a quarter for Proximate and Ultimate Analysis i.e. 4 test certificates in a year for each soild fuel 3) Purchase Order, where guaranteed GCV range is mentioned 4) DGR 5) MGR 6) Log Book | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document 6) FSA 7) Lab reports, 8) weighbridge reports 9) stacking reports
11.2 | Please provide the Gross Calorific Value (GCV), Total Consumption and Specific Fuel Consumption of Liquid Fuels (FO/LSHS/HSHS/Diesel/LDO/Any Other) as fired basis | Specific Fuel Consumption = Quantity of Fuel Energy input to Plant X Gross GCV of Fuel/ output generated from palnt |  | Primary-daily/ shift wise secondary- every 4 hours | 1) Purchase Order 2) Stores Receipt 3) SAP Entry in MM/PP/FI module 4) Annual Report 5) DGR 5) MGR | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document 6) FSA 7) Lab reports, 8) weighbridge reports 9) Flow Meter 10) Dip measurement in day tank
11.3 | Please provide the Gross Calorific Value, Total Consumption and Specific Fuel Consumption of Gaseous Fuels (NG/RLNG/APM/Others) as fired basis | Specific Fuel Consumption = Quantity of Fuel Energy input to Plant X Gross GCV of Fuel/ output generated from palnt |  | Primary-daily/ shift wise secondary- every 4 hours | 1) Purchase Order 2) Stores Receipt 3) SAP Entry in MM/PP/FI module 4) Annual Report 5) DGR 5) MGR | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document 6) FSA 7) Lab reports, 8) weighbridge reports 9) Flow Meter 10) Dip measurement in day tank
12 | Normalisation Factors to be considered during assessment year
12.1 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors
i | Please provide unitwise Average Operating Load (MW and Operating hours) caused by low ULF due to Coal Unavailability,due to Scheduling, due to backing down, or due to any other external factor for current year as well as for previous year | Ex: Average Operating Load due to Coal unavailability=Unit's Capacity (MW)-Unit's generation Loss due to coal unavailabilty (MW) where: Unit generation Loss due to coal unavailabilty (MW) = (Unit's Generation Loss (MU) due to coal unavailability x 1000)/Operating hours due to coal unavailability (Hrs) | During concurrnace period of low load due to external factor (multiple event), treatment of all the events could be combined into one event In case of concurrent losses due to external factors, all losses to be clubbed under one head. 1. External Factor: For example, for a 200 MW unit,if 20 MW is lost due to schedule, 10 MW due to backing down and 10 MW due to fuel concurrently for an operating hour of 1000 hours; then in that case, the lossees should be clubbed together to make it 40 MW loss for 1000 operating hours. Thus, in that case data to be entered should be 160 (average operating load due to schedule) for 1000 hours, leaving other factors (fuel, backing down etc blank 2. If there is concurrent MW loss due to internal factors and external factors, The internal factor loss could be ignored. Calculation sheet for alll these concurrent evernt should be prepared and kept ready for verification | Continuous, Daily, Monthly | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Generation Schedule from Load Despatch Centre 5) External Breakdown Report 6) Fuel Unavailability document/record from external agencies 7) Coal Linkage Document 8) Stores Stocks Register 9) SAP Entry in PP/SD/PM Module 10) Stocks duration report 11) Log Book | 1) Purchase order 2) Rail Racks details 3) Weighing Document 4) Shift Register 5) Shift Reports 6) Energy Meter Readings 7) Energy Management System
12.2 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors/Internal Factor
i | Please provide unit wise operation hours (Hours) caused by Forced Outage/ Unavailability, Planned Maintenance Outage/ Planned Unavailability and Average Operating Load (MW) and with Operating hours due to Internal factor for baseline year and Assessment year | Weighetd Operating Load = [Average Operating Load (MW) due to coal unavailability X operating Hour + Average Operating Load (MW) due to scheduling X Operating hours + Average Operating Load due to backing down X Operating Hour] / [ total average operating load (MW) X Total operating Hour] |  | Primary-Daily Secondary- hourly | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Generation Schedule from Load Despatch Centre 5) External Breakdown Report 6) Fuel Unavailability document/record from external agencies 7) Coal Linkage Document 8) Log Book | 1) Shift Register 2) Shift Reports 3) Energy Meter Readings 4) Energy Management System 5) Breakdown reports (Internal and External)
ii | Please provide the following Documents listed below:
i. Characteristics Curve of Unit Turbine Heat Rate Vs Load, from Original Equipment Manaufacturer (OEM)
ii. Unit wise HBD or Curve from Original Equipment Manufacturer (OEM) at various loads
iii. In case of non-availability of HBD or Curve, data from the similar Unit will be considered
iv. Design/PG Test Turbine Heat Rate documents
12.3 | APC Linked with PLF
a | Please enter the APC as per the baseline audit report |  |  | One Time | Annual Report | Audit Report
i | Please enter the APC as pet the APC trendline equation for AY and BY | The curve will be plotted w.r.t. % Loading Factor Vs % APC to Normalise the APC at low load due to low loading or PLF, if it is reduced due to external factor. The Load data of Plant and APC will be taken during Plant's stabilised condition. The equation with accuracy factor of R2=0.85 will be accepted for this purpose | DC to provide the trend line curve in Excel format. The curve should be drawn from the operating data of current year and avarage of baselin year in terms of % Plant Loading Vs the auxilliary power consumption (APC) in % during normal operation of the plant | Continuous, Daily, Monhtly, Yearly | 1) DGR 2) MGR 3) Annul Report 4) SAP Entry in PP/SD/PM Module | 1) Energy Meters 2) Daily Power Report 3) Energy Management System
12.4 | Startup and Stoppages due external factor/Unforeseen factors
A.i | Please provide total number of shutdown in a year separately operating through different fuel Gas/Coal due to Internal and external factor in Nos |  |  | Primary- Annual Secondary-As & when occurred | Annual Reports | Trip reports/ Shift Reports/ Synchronization communication
A.ii | Please provide total number of shutdown in a year due to external factor eparately operating through different fuel Gas/Coal due to external factor in Nos |  |  | Primary- Annual Secondary-As & when occurred | Annual Reports | Trip reports/ Shift Reports/ Synchronization communication
B.i | Please provide the Electrical Energy Consumption during shutdown due to external factor in MU |  |  | Primary- Annual Secondary-As & when occurred | 1) DGR 2) MGR 3) Annul Report 4) SAP Entry in PP/SD/PM Module | 1) Energy Meters 2) Daily Power Report 3) Energy Management System 4) Trip reports/ Shift Reports/ Synchronization communication
C | Please provide total number of Cold/Warm/Hot startup in a year due to external factor in Nos | DC to follow the defination of Cold/Worm/Hot start as defined in the OEM document of Turbine on temperature |  | Primary- Annual Secondary-As & when occurred | 1) OEM document for Turbine 2) DGR 3) MGR 4) Annul Report 5) SAP Entry in PP/SD/PM Module 6) External factor document | Trip reports/ Shift Reports/ Synchronization communication
12.5 | Increase in APC consumption due Environmental Compliance
i | Please provide the name, commitioning date , kw rating , actual operating hour and total energy consumptiion of equipments installed to meet the environmental complience in AY and BY |  |  | One time | 1) OEM Documents 2) Purchase order of equipment 3) Shift Log book 4) Shift Register | 1) Energy Meter reading 2) Energy Management System
12.6 | Additional Energy due to Unforeseen circumstances (External Factor) |  |  | Monthly | Monthly Generation/ operation reports | Efficiency Cell Reports
i | Please enter Total Thermal Energy consumption due to unforseen circumstances |  |  | Monthly | 1) Monthly Generation 2) Operation reports 3) Unforeseen Circumstances Documents | Efficiency Cell Reports
ii | Please enter Total Electrical Energy consumption due to unforseen circumstances |  |  | Monthly | 1) Monthly Generation 2) Operation reports 3) Unforeseen Circumstances Documents | Efficiency Cell Reports
13 | Documentation for Normalisation
i | The list of documents that shall be submitted by the DCs is mentioned. The DC shall submit the doc and write Yes/No in the relevant docuembt column | 1) For Normalisation factors, which became applicable due to external factors, authentic documents to be produced by DC for the baseline as well for the assessment year. In absence of these authentic documents, no Normalisation Factor will be applied/Considered. 2) While selecting "No" from the drop down list, the inbuilt calculation automatic treat the Normalisation for particular factor as zero. However, DC needs to submit an undertaking from the Authorised Signatory on non-availability of document
14 | Investment made and Saving Achieved
i | Investment, if any, during this period has to be mentioned with quantified savings in terms of million kcal of coal, lignte, petcoke, biomass/ waste
15 | Process Flow Diagram Attached
i | The process flow diagram has to be attached indicating the entire scheme of the system/ sub-system
Note | For Thermal Power Station firing Gas/ Oil/ Other Fuels in Boiler
Section 5 | All the relevant details with Gas fuel shall be entered | Unit Design Heat Rate (UDHR) = Turbine Heat Rate /Boiler Efficiency, |  | One time | OEM Curves and docuemts/ COD documents | PG Test Reports/ Certified reports on Fuel Change
Section 5.2 | All the relevant details with Oil/Other Fuel shall be entered | Station's Design Heat Rate = [UDHR1xC1 + UDHR2xC2+ UDHR3xC3………]/[C1+C2+C3…….] Where C1, C2, C3, …..= Unit Capacity in MW |  | One time | OEM Curves and docuemts/ COD documents | PG Test Reports/ Certified reports on Fuel Change
16 | Note
(i) | The hard copy/Printouts is to be signed by Authorised signatory, if SAP data is used as documents
17 | Abbreviations
MPR | Monthly Production Report
DPR | Daily Production Report
MM | Material Management
PP | Production and Planning
SD | Sales and Distribution
FI | Financial Accounting
PM | Plant Maintenance
EMS | Energy Management System

## Form-1
Form-1
Details of information regarding Total Energy Consumed and Specific Energy Consumption Per unit of Production (See Rule 3)
A. | General Details | Description
1 | Name of the Unit | 0
2 | i) Year of Establishment | 0
| (ii) Registration No (As provided by BEE) | 0
3 | Sector and Sub-Sector in which the Designated Consumers falls | Sector |  | Sub-Sector
|  | Sector - Thermal Power Plant |  | Coal/Lignite/Oil/Gas Fired
4. (i) | Complete address of DCs Unit location (including Chief Executive's name & designation) with mobile, telephone, fax nos. & e-mail. | , , , - , Telephone- , Fax- , Plant's Chief Executive Name-, , Telephone with STD Code- , Fax- , Mobile-, E-mail-
(ii) | Registered Office address with telephone, fax nos. & e-mail | Company's Chief Executive Name:,Designation:,Address:,City/Town/Village-,P.O.-, District-,State-,Pin-, Telephone-,Fax-
(iii) | Energy Manager's Name, designation, Registration No., Address, Mobile, Telephone, Fax nos. & e-mail | , , , EA/EM Registration No.- , Telephone-, Fax- , Mobile- , E-mail ID-
B. | Production details
5 | Manufacturing Industries notified as Designated Consumers
| Products | Unit | Previous Year | Current Year
(i) | Product 1 | Tonne
(ii) | Product 2 | Tonne
(iii) | Product 3 | Tonne
(iv) | Product (Please add extra rows in case of additional products) | Tonne
(v) | Total Equivalent Product | Tonne
C | Energy Consumption Details of Manufacturing Industries notified as Designated Consumers
6. (i) | Total Electricity Purchased from Grid/Other Source | Million kwh
(ii) | Total Electricity Generated | Million kwh
(iii) | Total Electricity Exported | Million kwh
(iv) | Total Electrical Energy Consumption | Million kwh
(v) | Total Solid Fuel Consumption | Million kCal
(vi) | Total Liquid Fuel Consumption | Million kCal
(vii) | Total Gaseous Fuel Consumption | Million kCal
(viii) | Total Thermal Energy Consumption | Million kCal
(ix) | Total Normalized Energy Consumption (Thermal+Electrical) | TOE
D | Specific Energy Consumption Details
7. i | Specific Energy Consumption(Without Normalization) | TOE/Tonne
ii | Specific Energy Consumption (Normalized) | TOE/Tonne
E | Power Plants notified as Designated Consumer
8. i. | Total Capacity | MW | 0 | 0
ii | Unit Configuration | No. of units with their capacity | 0 | 0
iii | Annual Gross Generation | MU | 0 | 0
iv | Annual Plant Load Factor (PLF) | % | 0 | 0
v | Station Gross Design Heat Rate | kcal/kWh | 0 | 0
vi | Station Gross Operative Heat Rate | kcal/kWh | 0 | 0
vii | Auxiliary Power Consumption | % | 0 | 0
viii | Operative Net Heat Rate | kcal/kWh | 0 | 0
ix | Operative Net Heat Rate (Normalized) | kcal/kWh |  | 0
F | Sector-Specific Details
S.No | Name of the Sector | Sub-Sector | Form in which the details to be furnished
(i) | Aluminium | Refinery/Smelter | Sa1
|  | Cold Rolling Sheet | Sa2
(ii) | Cement | Cement | Sb
(iii) | Chlor-Alkali | Chlor-Alkali | Sc
(iv) | Fertilizer | Fertilizer | Sd
(v) | Iron and Steel | Integrated Steel | Se1
|  | Sponge Iron | Se2
(vi) | Pulp and Paper | Pulp and Paper | Sf
(vii) | Textile | Composite | Sg1
|  | Fiber | Sg2
|  | Spinning | Sg3
|  | Processing | Sg4
(viii) | Thermal Power Plant | Thermal Power Plant | Sh
I/we undertake that the information supplied in the Form 1 and pro- forma is accurate to the best of my knowledge and the data furnished in Form 1 has been adhered to the data given in the concerned pro forma.
Authorised Signatory and Seal
Signature:-
Name of Energy Manager:
Name of Authorised Signatory |  |  | Registration Number:
Name of the Designated Consumer:
Full Address:-
Seal
Date

## General Information
Form-Sh (General Information)
Sector - Thermal Power Plant
1 | Name of the Thermal Power Station
2 | i) Year of Establishment
(ii) Registration No (As provided by BEE)
3 | Type of Thermal Power Plant | Coal/Lignite/Oil/Gas Fired | Coal/Lignite/Oil/Gas Fired
4 | Plant Contact Details & Address
a | Plant Address
i | City/Town/Village
ii | District
iii | State |  |  | Pin
iv | Telephone |  |  | Fax
b | Plant's Chief Executive Name
i | Designation
ii | Telephone with STD Code |  |  | Fax
iii | Mobile |  | E-mail
5 | Registered Office
i | Company's Chief Executive Name
ii | Designation
iii | Address
iv | City/Town/Village |  |  | P.O.
v | District
vi | State |  |  | Pin
vii | Telephone |  |  | Fax
6 | Energy Manager Details
i | Name
ii | Designation |  |  | Whether EA or EM
iii | EA/EM Registration No.
iv | Telephone |  |  | Fax
v | Mobile |  | E-mail ID

## Form Sh
Form Sh (Details of Generation and Energy Consumption)
Sector - Thermal Power Plant
1 | Name of Thermal Power Plant |  |  | 0
2 | Year of Establishment |  |  | 0
3 | Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
4 | Plant Details
Sr No | Item |  |  | Current/ Assessment/ Target Year (20.... 20....) | [7 empty] | Baseline Year (20.... 20....) | [7 empty] | Source of Data
i | Total Capacity (MW)
ii | Unit/Module Configuration (i.e. 3x100 + 2x250 + 2x500+ ------- etc.)
iii | Notified Baseline Net Heat Rate (kcal/kWh)
iv | Notified Target Net Heat Rate (kcal/kWh)
v | Notified Net Product output (Net Generation) in Million Units
vi | % Reduction Target for Percentage deviation in the Station Net Heat Rate as per Notificataion
5 | Unit /Module wise Design Data Details (For major fuel)
Sr No | Units@@ | Nomenclature of Units as per Standard Practice of TPPs | COD | Design Capacity | As Provided by Original Equipment Manufacturer (OEM) |  |  | As established during Performance Guarantee Test (PG Test) ** |  |  | Curve Equation/ (R2) |  |  |  |  | Load Vs Heat Rate or HBD (at 100% Load) as per curve | Design Gas Turbine Heat Rate at different condition |  |  | Design Fuel Type (Coal/Lignite/ Gas/Naptha/ Oil/Other) | Source of Data
[5 empty] | Boiler Efficiency | Turbine Heat Rate (Coal based TPP) | Unit Heat Rate* | Boiler Efficiency | Turbine Heat Rate (Coal based TPP) | Unit Heat Rate | OEM Curve or HBD data curve |  | Constant 1 | Constant 2 | Constant 3 | Turbine Heat Rate | Module Heat Rate with Naphtha (For Gas based Power station) | Module Heat Rate with Oil/Other Fuel (For Gas based Power station) | Module Heat Rate Open Cycle (Major Fuel)
|  |  | Date | MW | % | kcal/kWh | kcal/kWh | % | kcal/kWh | kcal/kWh | y=ax2-bx+c | R2 | a | b | c | kcal/kWh | kcal/kWh | kcal/kWh | kcal/kWh
i | Unit1 | [5 empty] | 0 |  |  | 0 | [9 empty] | Gas
ii | Unit2 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
iii. | Unit3 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
iv. | Unit4 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
v | Unit5 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
vi | Unit6 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
vii | Unit7 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
viii | Unit8 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
ix | Unit9 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
x | Unit10 | [5 empty] | 0 |  |  | 0 | [9 empty] | Coal
5.1 | Station Design Data Details *** |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0
5.2 | Unit /Module wise Design Data Details (For other fuel)
i | Unit1 | [5 empty] | 0 |  |  | 0 | [9 empty] | Gas
ii | Unit2 | [5 empty] | 0 |  |  | 0 | [9 empty] | Gas
iii. | Unit3 | [5 empty] | 0 |  |  | 0 | [9 empty] | Oil
iv. | Unit4 | [5 empty] | 0 |  |  | 0 | [9 empty] | Oil
v | Unit5 | [5 empty] | 0 |  |  | 0 | [9 empty] | Oil
5.3 | Note
i | *** Weighted Average except for Design Capacity [For ex (Coal Fired): Station Design Heat Rate = {(DGHR 1 x Capacity 1 + DGHR 2 x Capacity2 + -----------) / (Total Capacity of Station)}] and [For ex (Gas Turbine):Station Operating Heat Rate={(Module HR 1 x Capacity 1 + Module HR 2 x Capacity2 + -----------) / (Total Capacity of Station Module)}
ii | ** To be indicated only if OEM certified design or PG Test report is available and the same can be produced as documentry proof, whenever required. If gas/liquid fuel is used, the Design/PG value for gas/liquied fuel may be given separately.
iii | * For Coal Based TPP- Unit Heat Rate (kcal/kWh) = [ Turbine Heat Rate (kcal/kWh) / Boiler Efficiency (%) ]
iv | @For Gas Turbine- Module Heat Rate (kcal/kWh) = [Design Fuel Input (NCV-kcal)/ Design Gross Out Put (kWh)]
v | @@ Module stands for Gas Power Station (referred as Combined setup of GT and ST)
vi | For other Fuel data, plant to insert the data in section 5.2 with Unit Nos
6 | Unit/Module wise Operating Data Details
Sr No | Units |  |  | Current/ Assessment/ Target Year (20.... 20....) | [7 empty] | Baseline Year (20.... 20....) | [7 empty] | Source of Data
|  |  |  | Operating Load # |  | Loading Factor |  | Gross Generation |  | Unit Gross Heat Rate## |  | Operating Load |  | Loading Factor |  | Gross Generation |  | Unit Gross Heat Rate ##
|  |  |  | MW |  | % |  | MU |  | kcal/kWh |  | MW |  | % |  | MU |  | kcal/kWh
i | Unit1
ii | Unit2
iii. | Unit3
iv. | Unit4
v | Unit5
vi | Unit6
vii | Unit7
viii | Unit8
ix | Unit9
x | Unit10
6.1 | Station Operating Data Details ## |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6.2 | Note
i | # Unit/Module Gross Generation in kWh in a year / Plant running hours in hrs in a year
ii | ## Heat rate = Total Fuel Consumed in the unit or module /Total Generation
iii | Weighted Average except for Operating Capacity [For ex (Coal Fired): Station Operating Heat Rate = {(OGHR 1 x Capacity 1 + OGHR 2 x Capacity2 + -----------) / (Total Capacity of Station)}] and [For ex (Gas Turbine):{(Station Operating Heat Rate=Module HR 1 x Capacity 1 + Module HR 2 x Capacity2 + -----------) / (Total Capacity of Station Module)}
7 | Station's Generation, PLF & Other Details
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (20.... 20....) | [6 empty] | Baseline Year (20.... 20....) | [7 empty] | Source of Data
i | Station Installed Capacity |  |  | MW | 0 | [6 empty] | 0
ii | If COD of some unit(s) is in between the year, total station's weighted capacity for the year $ |  |  | MW | [7 empty] | 630
iii | Actual Gross Generation |  |  | MU | 0 | [6 empty] | 0
iv. | Plant Availability Factor |  |  | % | 1 | [6 empty] | 1
v | Annual PLF (Weighted)$$ |  |  | %
vi | Auxiliary Power Consumption $$$ (as per Sr. no 9(iv)) |  |  | MU | 0 | [6 empty] | 0
vii | Auxiliary Power Consumption $$$ (as per Sr No 7(iii) &7(vi)) |  |  | % | 0 | [6 empty] | 0
viii | Operating Gross Heat Rate |  |  | kcal/kWh | 0 | [6 empty] | 0
ix | Net Operating Heat Rate (kcal/kWh) $$$$ |  |  | kcal/kWh | 0 | [6 empty] | 0
x | Average PLF during Baseline year as per baseline energy audit reports |  |  | %
xi | Actual PLF as reported to CERC/SERC |  |  | %
xii | Operation Norms for Thermal Power Stations Gross Heat Rate Tariff Period - 2014 - 19 as per CERC/SERC |  |  | kcal/kWh
xiii | Station Net Operating Heat Rate as per Notification (Baseline) |  |  | kcal/kWh | [7 empty] | 0
xiv | Station Net Target Heat Rate as per Notification (Baseline) | [10 empty] | 0
7.1 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii) in case of Gas based Power Station or Thermal Oil-Gas based Plant)
Sr No | Item | Unit | Current/ Assessment/ Target Year (20.... 20....) | [8 empty] | Baseline Year (20.... 20....)
|  |  | Actual Gross Generation-Closed Cycle |  |  | Actual Gross Generation-Open Cycle due to Internal factor |  |  | Actual Gross Generation-Open Cycle due to External factor |  |  | Actual Gross Generation-Closed Cycle |  |  | Actual Gross Generation-Open Cycle due to Internal factor |  |  | Actual Gross Generation-Open Cycle due to External factor |  |  | Source of Data
|  |  | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel
i | Unit1 | MU
ii | Unit2 | MU
iii. | Unit3 | MU
iv. | Unit4 | MU
v | Unit5 | MU
vi | Unit6 | MU
vii | Unit7 | MU
viii | Unit8 | MU
ix | Unit9 | MU
x | Unit10 | MU
| Total | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.2 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii), 7(vi) in case of Gas based Power Station)
Sr No | Item | Units | Current/ Assessment/ Target Year (20.... 20....) | [8 empty] | Baseline Year (20.... 20....) | [8 empty] | Source of Data
|  |  | Gas |  |  | Naptha |  |  | Oil/Other Fuel |  |  | Gas |  |  | Naptha |  |  | Oil/Other Fuel
i | Auxiliary Power Consumption | MU
ii | Actual Gross Generation-Closed Cycle | MU | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
iii | Actual Gross Generation -Open Cycle due to internal factor | MU | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
iv | Actual Gross Generation-Open Cycle due to external factor | MU | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
v | Actual Gross Generation |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
vi | Auxiliary Power Consumption | % | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7.3 | Remarks
i | $ For example : if the COD of a 200 MW unit is 1st October in the current year, its weighted capacity for the whole year is 100 MW
ii | $$ Example-For Calculating ULF of the unit commissioned during the year : if the COD of a 200 MW unit is 1st October and PLF for the remaining period is 80% , its weighted capacity for the whole year is 100 MW, with weighted for whole year PLF stands at 40%
iii | $$$Power Consumption for Colony & Construction to be excluded
iv. | $$$$Net Heat Rate = [Gross Heat Rate / (1 - % APC)]
v | Note:In case of Gas based Power Station, the APC% for Gas/Liquid fuel may be given separately
8 | Details of Electricity Purchased from the Grid (MUs)
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (20.... 20....) | [6 empty] | Baseline Year (20.... 20....) | [7 empty] | Source of Data
i | Purchased Electricity |  |  | MUs | ` | [6 empty] | w
ii | Reason
9 | Details of Electricity Generated and Auxiliary Power Consumption
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (20.... 20....) | [6 empty] | Baseline Year (20.... 20....) | [7 empty] | Source of Data
i | Total Gross Generation of Electricity |  |  | MU | 0 | [6 empty] | 0
ii | Total Net Electricity Supplied to Grid |  |  | MU | 0 | [6 empty] | 0
iii | Electricity Consumption-Colony/Construction |  |  | MU
iv. | Total Electricity used inhouse for Power Generation i.e. APC (Without colony, construction & others consumption) |  |  | MU
v | Any other (specify) |  |  | MU
10 | Unitwise Fuel Analysis Details (As Fired Basis)@ (Not to be filled up for Gas based Power Station)
10. 1. | Coal/Lignite Fuel
A. | Unit-1
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3 / Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
B | Unit-2
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
C | Unit-3
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
D | Unit-4
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
E | Unit-5
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
F | Unit-6
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
G | Unit-7
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
H | Unit-8
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
I | Unit-9
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
J | Unit-10
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Baseline Year (20.... 20....) (Weighted Average)@@ | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3)
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
10.1.1 | Note
i | If Ultimate Analysis value is not available with DCs, Conversion from Proximate to Ultimate will be applied conversion formulae. %C = 0.97C+ 0.7(VM+0.1A) - M(0.6-0.01M) %H2= 0.036C + 0.086 (VM -0.1xA) - 0.0035M2(1-0.02M) %N2= 2.10 -0.020 VM Where: C= % of fixed carbon , A= % of ash ,VM= % of volatile matter, M= % of moisture
ii | In case of difference in Design Coal Quality for different units, Coal analysis to be given unitwise, otherwise enter the same parameter
10.1.2 | @ Attach all necessary Documents -
A | Coal Analysis:
i | Operating Coal Quality- Monthly average of the lots (As Fired Basis),Test Certificate for Coal Analysis including Proximate and Ultimate analysis (Minimum of 1 Samples Test from Government Lab for cross verification- Quarterly)
ii | Performance Guarantee Test (PG Test) report from Original Equipment Manufacturer (OEM)
iii | Design Coal Analysis Document as per OEM
B | Boiler Efficiency
i | Design Boiler Efficiency Document from Original Equipment Manufacturer (OEM)
ii | @@ Weighted Average for the year: the sum of the tested coal of each lot as fired multiplied with the quantity of each lot , to be divided by the total fuel quantity during the year.
10.2 | Gas/Naptha/Furnace Oil Chemical and Physical Analysis used in Gas based Power Plant
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/Assessment/Target Year (20... 20...) |  |  |  |  | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3) |  | Source of Data
10.2.1 | Gas Chemical and Physical Analysis
i | Methane (CH4) |  |  | % | [13 empty] | 0
iii | Ethane (C2H6) |  |  | % | [13 empty] | 0
iv | Propane (C3H8) |  |  | % | [13 empty] | 0
v | Other Hydro Carbons (C4+) |  |  | % | [13 empty] | 0
vi | Hydrogen |  |  | % | [13 empty] | 0
vii | Nitrogen |  |  | % | [13 empty] | 0
viii | Wobbe Index |  |  | No | [13 empty] | 0
ix | Methane No |  |  | No | [13 empty] | 0
x | Relative density (Specific Gravity) |  |  | kg/NM3 | [13 empty] | 0
xi | GCV |  |  | kcal/NM3 | [13 empty] | 0
xii | NCV |  |  | kcal/NM3 | [13 empty] | 0
10.2.2 | Naptha Analysis
i | GCV |  |  | kcal/kg | [13 empty] | 0
ii | NCV |  |  | kcal/kg | [13 empty] | 0
10.2.3 | Furnace Oil Analysis
i | GCV |  |  | kcal/kg | [13 empty] | 0
0
10.2.2 | Remarks:
i | Gas based Power station, The design heat rate given by either OEM or taken from HBD for the site rated ambient condition or PG test value will be taken for calculation
ii | Due to some unforeseen reasons, if Gas Turbine is operating in Open Cycle, separate documents should be maintained by the Plant for baseline as well as for assessment year
iii | Gas Supplier Fuel Analysis Documents should be available with Plant.
iv | For Mixed fuel such as Gas, Furnace Oil & Naphtha, documents related to design details of Gas/Furnace Oil/Naphtha maybe given separately.
11 | Details of Fuel Consumption (As Fired Basis)
Sr No | Item |  |  | Units | Current/Assessment/Target Year (20... 20...) | [6 empty] | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3) |  | Source of Data
11.1 | Solid Fuel
a | Coal/Lignite
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific Value |  |  | kcal/kg © | [13 empty] | 0
iii | Total Coal/Lignite Consumption |  |  | Tonne | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Coal/Lignite Consumption |  |  | Kg/kWh | [13 empty] | 0
b | Imported Coal
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific Value |  |  | kcal/kg © | [13 empty] | 0
iii | Total Coal Consumption |  |  | Tonne | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Coal Consumption |  |  | Kg/kWh | [13 empty] | 0
c | Other Solid fuels
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg © | [13 empty] | 0
iii | Total other fuel Consumption |  |  | Tonne | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific other fuel Consumption |  |  | Kg/kWh | [13 empty] | 0
11.2 | Liquid Fuel ℗
a | Liquid Fuel (LSHS/HSHS/LDO/Any Other)
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg© | [13 empty] | 0
iii | Total Oil Consumption |  |  | KL | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Oil Consumption for Coal/Gas fired Power Station |  |  | ml/kWh | [13 empty] | 0
v | Specific Oil Consumption for DG Set Station |  |  | Litre/kWh | [13 empty] | 0
b | Liquid Fuel (Naptha/ FO/Any Other)
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg© | [13 empty] | 0
iii | Total Oil Consumption |  |  | KL | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Oil Consumption for Coal/Gas fired Power Station |  |  | ml/kWh | [13 empty] | 0
v | Specific Oil Consumption for DG Set Station |  |  | Litre/kWh | [13 empty] | 0
c | Liquid Fuel (Any Other)
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg© | [13 empty] | 0
iii | Total Oil Consumption |  |  | KL | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Oil Consumption for Coal/Gas fired Power Station |  |  | ml/kWh | [13 empty] | 0
v | Specific Oil Consumption for DG Set Station |  |  | Litre/kWh | [13 empty] | 0
11.3 | Gaseous Fuel
a | Type of Gas Fuel |  |  | NG
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/SCM | [13 empty] | 0
ii | Gross Calorific value |  |  | (kcal/NM³)© | [13 empty] | 0
iii | Total Gas Consumption |  |  | Million NM³ | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Gas Consumption |  |  | NM³/kWh | [13 empty] | 0
b | Type of Gas Fuel |  |  | RLNG/LNG/ Others
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/SCM | [13 empty] | 0
ii | Gross Calorific value |  |  | (kcal/NM³)© | [13 empty] | 0
iii | Total Gas Consumption |  |  | Million NM³ | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Gas Consumption |  |  | NM³/kWh | [13 empty] | 0
c | Type of Gas Fuel |  |  | APM
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/SCM | [13 empty] | 0
ii | Gross Calorific value |  |  | (kcal/NM³)© | [13 empty] | 0
iii | Total Gas Consumption |  |  | Million NM³ | [7 empty] | 0 |  | 0 |  | 0 |  | 0
iv | Specific Gas Consumption |  |  | NM³/kWh | [13 empty] | 0
11.3.1 | Note
i | ℗Note: In case of Liquid fuels, take care of Density during calculations
ii | ©Weighted Average GCV i.e. sum of Heat value found in kcal in each lot on As Fired Basis, & analysed (tested) and fired during the year divided by total quantity of fuel fired during the financial year
12.1 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors
Sr No | Units |  |  | Current/Assessment/Target Year (20... 20...) | [7 empty] | Baseline Year (BY) Average (20…. 20….) | [7 empty] | Source of Data
|  |  |  | Average Operating Load (MW) caused by low ULF/MLF due to Fuel Unavailability @ |  | Average Operating Load (MW) caused by low ULF/MLF due to Scheduling @ |  | Average Operating Load (MW) caused by low ULF/MLF due to backing down@ |  | Average Operating Load (MW) caused by low ULF/MLF due to any other external factor@ |  | Average Operating Load (MW) caused by low ULF/MLF due to Fuel Unavailability @ |  | Average Operating Load (MW) caused by low ULF/MLF due to Scheduling @ |  | Average Operating Load (MW) caused by low ULF/MLF due to backing down@ |  | Average Operating Load (MW) caused by low ULF/MLF due to any other external factor@
|  |  |  | MW | Operating Hours | MW | Operating Hours | MW | Operating Hours | MW | Operating Hours | MW | Operating Hours | MW | Operating Hours | MW | Operating Hours | MW | Operating Hours
i | Unit1 | [20 empty] | 1200
ii | Unit2 | [20 empty] | 815.3153
iii. | Unit3
iv. | Unit4
v | Unit5
vi | Unit6
vii | Unit7
viii | Unit8
ix | Unit9
x | Unit10
| Total |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1.1 | @ External Factors:Non-Avaialability of fuel/schedule/backing down/any other external factor/Unforeseen factors
12.2 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors/Internal Factor
Sr No | Units |  | Capacity | Current/Assessment/Target Year (20... 20...) | [7 empty] | Baseline Year (BY) Average (20…. 20….) | [7 empty] | Source of Data
|  |  |  | Reserve Shutdown | Forced Outage/ Unavailability | Planned Maintenance Outage /Planned Unavailability | Unit Availability Factor | Average Operating Load (MW) caused by low ULF/MLF due to Internal factor | Operating hours | Average Operating Load (MW) caused by low ULF/MLF due to external factor @ | Average Operating hours at Low ULF/MLF | Reserve Shutdown | Forced Outage/ Unavailability | Planned Maintenance Outage/ Planned Unavailability | Unit Availability Factor | Average Operating Load (MW) caused by low ULF/MLF due to Internal factor | Operating hours | Average Operating Load (MW) caused by low ULF/MLF due to external factor @ | Average Operating hours at Low ULF/MLF
|  |  | MW | Hrs | Hrs | Hrs |  | MW | Hrs/Annum | MW | Hrs/Annum | Hrs | Hrs | Hrs |  | MW | Hrs/Annum | MW | Hrs/Annum
i | Unit1 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
ii | Unit2 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
iii | Unit3 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
iv | Unit4 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
v | Unit5 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
vi | Unit6 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
vii | Unit7 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
viii | Unit8 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
ix | Unit9 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
x | Unit10 |  | 0 |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 1 |  |  | 0 | 0
xi | Total |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
@ External Factors:Non-Availability of fuel/schedule/backing down/any other external factor
12.2.1 | Documents Required
i | Characteristics Curve of Unit/Module Turbine Heat Rate Vs Load, from Original Equipment Manufacturer (OEM)
ii | Unit/Module wise HBD or Curve from Original Equipment Manufacturer (OEM) at various loads
iii | In case of non-availability of HBD or Curve, data from the similar Unit/Module will be considered
iv. | Design/PG Test Turbine/Module Heat Rate documents
12.3 | APC Linked with PLF
Sr No | APC during Baseline year as per baseline energy audit reports |  |  | Current/Assessment/Target Year (20... 20...) | [7 empty] | Baseline Year (BY) Average (20…. 20….) | [7 empty] | Source of Data
|  |  |  | APC Vs Load Curve Equation |  | Constant 1 |  | Constant 2 |  | Constant 3 |  | APC Vs Load Curve Equation |  | Constant 1 |  | Constant 2 |  | Constant 3
| % |  |  | -ax2-bx+c | R2 | a |  | b |  | c |  | -ax2-bx+c | R2 | a |  | b |  | c
i
12.3.1 | NOTE
i | The curve will be plotted w.r.t. Load Vs % APC to Normalise the APC at low load due to low loading or PLF, if it is reduced due to external factor. The Load data of Plant and APC will be taken during Plant's stabilised condition. The equation with accuracy factor of R2=0.85 will be accepted for this purpose
12.4 | Startup and Stoppages due external factor/Unforeseen factors
A | Nos of Startup and Shutdowns
Sr No | Item |  |  | Units | Current/Assessment/Target Year (20... 20...) | [6 empty] | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3) |  | Remarks
[5 empty] | GTG (Gas) |  |  | STG (Coal/Gas/Diesel) |  |  |  | GTG (Gas) | STG (Coal/Gas/Diesel) | GTG (Gas) | STG (Coal/Gas/Diesel) | GTG (Gas) | STG (Coal/Gas/ Diesel) | GTG (Gas) | STG (Coal/Gas/ Diesel)
i | Total Number of Shutdown in a year (Internal and External) |  |  | Nos | [13 empty] | 0 | 0
ii | Total Number of Shutdown in a year due to external factor |  |  | Nos | [13 empty] | 0 | 0
B | Energy Consumption during Shutdowns due to external factor
i | Total Electrical Energy consumption during shutdowns due to external factor |  |  | MU | [13 empty] | 0
12.4.1 | The DC may submit separate Excel sheet for additional information required for Heat Rate calculation or Normalisation for different module combination or load (Start/Stop)
C | Energy Consumption during Startups (Cold/Warm/Hot) due to external factor for Coal based Thermal Power Plant
Sr No | Units |  |  | MW | Current/Assessment/Target Year (20... 20...) |  |  | Year 1 |  |  | Year 2 |  |  | Year 3/ Previous Year (20.... 20....) |  |  | Baseline Year [BY] Average (20…. 20…) |  |  | Remarks
[5 empty] | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start
[5 empty] | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos | Nos
i | Unit1 |  |  | 0 | [12 empty] | 0 | 0 | 0
ii | Unit2 |  |  | 0 | [12 empty] | 0 | 0 | 0
iii. | Unit3 |  |  | 0 | [12 empty] | 0 | 0 | 0
iv. | Unit4 |  |  | 0 | [12 empty] | 0 | 0 | 0
v | Unit5 |  |  | 0 | [12 empty] | 0 | 0 | 0
vi | Unit6 |  |  | 0 | [12 empty] | 0 | 0 | 0
vii | Unit7 |  |  | 0 | [12 empty] | 0 | 0 | 0
viii | Unit8 |  |  | 0 | [12 empty] | 0 | 0 | 0
ix | Unit9 |  |  | 0 | [12 empty] | 0 | 0 | 0
x | Unit10 |  |  | 0 | [12 empty] | 0 | 0 | 0
12.4.1 | Documents
i | APC consumption records during startups and Shutdowns
ii | Fuel consumption (Coal/Lignite/Liquid Fuel/NG) Records during Cold/Warm/Hot startups
12.5 | Increase in APC consumption due to Environmental compliance
Sr No | Name of the Major Equipment Installed |  |  | Current/Assessment/Target Year (20... 20...) | [7 empty] | Baseline Year (BY) Average (20…. 20….) | [7 empty] | Source of Data
|  |  |  | Capacity | Section |  |  | Date of Commissioning | Additional Electrical Energy Consumption | Additional Thermal Energy Consumption | Remarks | Capacity | Name |  |  | Date of Commissioning | Additional Thermal Energy Consumption | Additional Electrical Energy Consumption | Remarks
[8 empty] | Date | MU | Million kcal | [5 empty] | Date | MU | Million kcal
i
ii
iii
iv
v
vi
vii
viii
ix
x
| Total | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
12.5.1 | Documents required related to Environmental compliance
i | The DCs have to maintain documents for additional installation of Environmental Equipment- Commissioning details, Energy meter reading etc
ii | Document of CPCB/SPCB
12.6 | Additional Energy due to Unforeseen circumstances (External Factor)
Sr No | Item |  |  | Units | Current/Assessment/Target Year (20... 20...) | [6 empty] | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3) |  | Source of Data
i | Total Electrical Energy consumption due to unforeseen circumstances (external factor) |  |  | MU | [13 empty] | 0
ii | Total Thermal Energy consumption due to unforeseen circumstances (external factor) |  |  | Million kcal | [13 empty] | 0
13 | Documentation for Normalisation
Sr No | Item |  |  |  | Current/Assessment/Target Year (20... 20...) | [6 empty] | Year 1 |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | Average (Yr 1, Yr 2 & Yr 3) |  | Source of Data
(i) | NF-1 Coal Quality -Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(ii) | NF-2 PLF-Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(iii) | NF-3 APC PLF-Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(iv) | NF-3.1 APC CQ Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(v) | NF-3.2 APC CQ Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(vi) | NF-4 Gas Fuel Mix Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(vii) | NF-5 Gas OC Cycle Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(viii) | NF-6 Gas NCV-Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(ix) | NF-7 Others Factors-Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
14 | Investment made and Saving Achieved |  |  | Annual
a | Investment made for achieving target |  |  | Million Rs
b | Thermal Energy Saving achieved during the year
b.1 | Solid Fuel
b.1.1 | Coal |  |  | Million kcal | [13 empty] | 0
b.1.2 | Lignite |  |  | Million kcal | [13 empty] | 0
b.1.3 | Petcoke |  |  | Million kcal | [13 empty] | 0
b.1.4 | Biomass/Waste |  |  | Million kcal | [13 empty] | 0
b.2 | Liquid Fuel (HSD/LDO/FO/Others) |  |  | Million kcal | [13 empty] | 0
b.3 | Gaseous Fuel (LPG/Propone/NG/CNG/PNG/LNG/Others) |  |  | Million kcal | [13 empty] | 0
c | Electrical Saving achieved during the year |  |  | Lakh kWh | [13 empty] | 0
15 | Process Flow Diagram Attached |  |  | Yes/No | Yes | [6 empty] | Yes | [5 empty] | Yes
Please enter numeric values or leave blank
0 | Please eneter numeric value or "0"
Fomulae Protected
Data not to be filled
Yes | Select from the list Yes or No
We ……………………………………………….........................…..........................undertake that information furnished in the Sector Specific Form I are complete and accurate to the best of my knowledge. I also undertake that the information provided for Normalisation is limited to external factors only.
| (Signature of the Energy Manager) | [12 empty] | (Signature of the Chief Executive)
| Name & designation of the Energy Manager: | [12 empty] | Name & designation of the Chief Executive:
EM/EA No:
Mobile No:
Organisation Seal:
Date:
Place:

## Summary Sheet
Form Sh-Summary Sheet
Name of the Thermal Power Station |  |  | 0
Type of Thermal Power Station |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Basis/Calculation | Unit | Assessment Year (AY) | Baseline Year (BY) | Remarks
A | Station Configuration
A.1 | Total Capacity | As per Form Sh (4 (i)) | MW | 0 | 0
A.2 | Unit Configuration | As per Form Sh (4 (ii)) |  | 0 | 0
A.3 | Year of Establishment | As per Form Sh (2) | Year | 0 | 0
A.4 | Notified Baseline Net Heat Rate (kcal/kWh) | As per Form Sh (4 (iii)) | kcal/kWh |  | 0
A.5 | Notified Target Net Heat Rate (kcal/kWh) | As per Form Sh ( 4 (iv)) | kcal/kWh |  | 0
A.6 | Notified Net Product output (Net Generation) in Million Units | As per Form Sh ( 4 (v)) | MU |  | 0
A.7 | % Reduction Target for Percentage deviation in the Station Net Heat Rate as per Notification | As per Form Sh ( 4 (vi)) | % |  | 0
A.8 | Difference of Notified Baseline Net Heat Rate and Notified Net Heat Rate | (A.4)-(A.5) | kcal/kWh |  | 0
B | Station Design Configuration
B.1 | Station Gross Heat Rate |  | kcal/kwh | 0 | 0
B.2 | Boiler Efficiency |  | % | 0 | 0
C | Station Operating Configuration
C.1 | Gross Generation | As per Form Sh (6. 1) - 'Form Sh'!I49 | MU | 0 | 0
C.2 | Plant Load Factor (PLF) |  | %
C.3 | Loading Factor | As per 'NF-3 (14) - 'NF-3 APC'!E18 | % | 0 | 0
C.4 | Gross Operating Heat Rate | As per Form Sh (6. 1) - Form Sh'!K49 | kcal/kwh | 0 | 0
C.5 | Auxiliary Power Consumption (APC) | As per Form Sh (7. (vi)) - Form Sh'!F62 | MU | 0 | 0
C.6 | Auxiliary Power Consumption (APC%) | As per Form Sh (7. (vii)) - Form Sh'!F63 | % | 0 | 0
D | Heat Rate Configuration and Baseline Target Setting
D.1 | Station Design Net Heat Rate (DNHR) | B. 1 / (1- C. 6/100) | kcal/kwh |  | 0
D.2 | Station Operating Net Heat Rate (ONHR) | C.4 /(1- C.6 /100) | kcal/kwh |  | 0
D.3 | Difference in DNHR and ONHR | BY - (D.2 - D.1 ) | kcal/kwh |  | 0
D.4 | Deviation % from DNHR | D.3 *100/D.1 | % |  | 0
D.5 | Reduction Target for Deviation in Net Station Heat Rate (%) | AY = IF(BY(D.4) <=5, 10, IF(AND(BY(D.4) >5, BY(D.4)<=10), 17, IF(AND(BY(D.4) >10, BY(D.4)<=20), 21, IF(BY(D.4)>20, 24,0)))), BY = A.7 | % | 10 | 10
D.6 | Target Net Heat Rate | (D.5) x (D.3)/100 | kcal/kwh |  | 0
D.7 | Baseline Normalisation | (A.8)-(D.6) | kcal/kwh |  | 0
E | Normalisation in Operating Parameters
E.1 | Coal Quality
E.1.1 | Boiler Efficiency due to Coal Quality | As per NF-1 Coal Quality , S. No. 18 | % | 0
E.1.2 | Station Turbine Heat Rate to be Normalised due to Coal Quality | As per NF-1 Coal Quality , S. No. 16 | kcal/kwh | 0
E.2 | PLF
E2.1 | Weighted Station Design Turbine Heat Rate | As per NF-2 PLF Sr. No. 21 | kcal/kwh | 0
E2.2 | Normalised Station Design Turbine Heat Rate due to ULF as compared to BY | As per NF-2 PLF Sr. No. 22 | kcal/kwh | 0
E2.3 | Difference of Turbine Heat rate between Normalised Design Heat Rate and Design Heat Rate | As per NF-2 PLF Sr. No. 23 | kcal/kwh | 0
E.3 | APC
E.3.1 | Operating Gross Heat Rate | C.4 | kcal/kwh | 0
E.3.2 | Auxiliary Power Consumption (APC %) | C. 6 | % | 0
E.3.3 | Operating Net Heat Rate | C.4 /(1- C. 6/100) | kcal/kwh | 0
E.3.4 | Normalised Auxiliary Power Consumption (N-APC%) | As Per NF-3 APC Sr. No. 19 | % | 0
E.3.5 | Normalised Operating Net Heat Rate | AY = E.3.1 /(1-E.3.4 /100) | kcal/kwh | 0
E.3.6 | Heat Rate Normalisation for APC | (E.3.3 - E.3.5) | kcal/kwh | 0
E.3.7 | Coal Quality effect in APC
E.3.7.1 | Total Energy to be normalised due to Coal Quality effect in APC | NF-3.1 APC CQ [16] +NF-3.2 APC CQ [14] | Million kcal | 0
E.3.7.2 | Heat Rate Normalisation for Coal Quality effect in APC | E.3.7.1/C.1 | kcal/kwh | 0
E.4 | Others
E.4.1 | Total Energy to be normalised due to Start-ups/ Shutdowns/Environmental Concern/Unforeseen Circumstances | As per 'NF-7 Others' Sr. No. 10 | Million kcal | 0
E.4.2 | Heat Rate Normalisation for others | E.4.1 /(C.1-C.5) | kcal/kwh | 0
E.5 | Gas Fuel Mix
E.5.1 | Notion energy for Fuel Mix to be Normalised for station | As per 'NF-4 Gas Fuel Mix' Sr No 12 | Million kcal | 0
E.5.2 | Heat Rate Normalisation for Gas Fuel mix | AY = E.5.1 / C.1 | kcal/kwh | 0
E.6 | Gas OC Cycle
E.6.1 | Notional energy for Gas OC Cycle to be Normalised for station | As per NF-5 Gas OC Cycle' Sr. No. 12 | Million kcal | 0
E.6.2 | Heat Rate Normalisation for Gas OC Cycle | AY = E.6.1 / C.1 | kcal/kwh | 0
E.7 | Gas Quality
E.7.1 | Notional energy for Gas Quality to be Normalised for station | NF-6 Gas NCV [7] | Million kcal | 0
E.7.2 | Heat Rate Normalisation for Gas Quality | E.7.1/C.4 | kcal/kwh | 0
F | Coal/Oil-Gas Based Thermal Power plant Normalised Operating Heat Rate Calculation
F.1 | Operating Heat Rate
F.1.1 | Station Operating Gross Heat Rate | IF('General Information' Sr. No. 3 ="Coal/Lignite/Oil/Gas Fired",C.4,"Not Applicable") | kcal/kwh | 0
F.1.2 | Coal Based Thermal Power Plant Station Operating Net Heat Rate without Normalisation | IF('General Information' Sr. No. 3 ="Coal/Lignite/Oil/Gas Fired",F.1.1/(1-C.6/100),"Not Applicable") | kcal/kwh | 0
F.2 | Normalisation
F.2.1 | Coal Quality Normalisation | E.1.2 | kcal/kwh | 0
F.2.2 | PLF Normalisation | E.2.3 | kcal/kwh | 0
F.2.3 | APC Normalisation | E.3.6+E3.7.2 | kcal/kwh | 0
F.2.4 | Others Normalisation | E.4.2 | kcal/kwh | 0
F.3 | Coal Based Thermal Power plant Normalised Operating Net Heat Rate | IF('General Information' Sr. No. 3 ="Coal/Lignite/Oil/Gas Fired",F.1.2 -F.2.1 -F.2.2 - F.2.3 - F.2.4-D.7,"Not Applicable") | kcal/kwh | 0
G | Gas Based Thermal Power plant Normalised Operating Heat Rate Calculation
G.1 | Oprating Heat Rate
G.1.1 | Station Gross Operating Heat Rate | IF(OR('General Information' Sr. No. 3 ="Gas Turbine (Open Cycle)", 'General Information' Sr. No. 3 ="Combined Cycle Gas Turbine (CCGT)"),C.4 ,"Not Applicable") | kcal/kwh | Not Applicable
G.1.2 | Gas Based Thermal Power Plant Station Net Operating Heat Rate without Normalisation | IF(OR('General Information' Sr. No. 3 ="Gas Turbine (Open Cycle)",'General Information' Sr. No. 3 ="Combined Cycle Gas Turbine (CCGT)"),(G.1.1/(1- C.6/100)),"Not Applicable") | kcal/kwh | Not Applicable
G.2 | Normalisation
G.2.1 | PLF Normalisation | E2.3 | kcal/kwh | 0
G.2.2 | Gas Fuel Mix Normalisation | E.5.2 | kcal/kwh | 0
G.2.3 | Gas OC Cycle Normalisation | E.6.2 | kcal/kwh | 0
G.2.4 | APC Normalisation | E.3.6 | kcal/kwh | 0
G.2.5 | Gas Quality Normalisation | E7.2 | kcal/kwh | 0
G.2.6 | Others Normalisation | E.4.2 | kcal/kwh | 0
G.3 | Gas Based Thermal Power Plant Normalised Operating Net Heat Rate | IF(OR('General Information' Sr. No. 3 ="Gas Turbine (Open Cycle)",'General Information' Sr. No. 3 ="Combined Cycle Gas Turbine (CCGT)"),G.1.2 - G.2.1 - G.2.2 -G.2.3 - G.2.4-G.2.5-G.2.6-D.7,"Not Applicable") | kcal/kwh | Not Applicable
H | Diesel Generator Normalised Operating Heat Rate Calculation
H.1 | Operating Heat Rate
H.1.1 | Station Gross Operating Heat Rate | IF(D25="DG Set",E81,"Not Applicable") | kcal/kwh | Not Applicable
H.1.2 | Diesel Generator Operating Net Heat Rate without Normalisation | IF(D25="DG Set",E81/(1-E42/100),"Not Applicable") | kcal/kwh | Not Applicable
H.2 | Normalisation
H.2.1 | PLF Normalisation | E2.3 | kcal/kwh | 0
H.2.2 | Others Normalisation | E4.2 | kcal/kwh | 0
H.3 | Diesel Generator Plant Normalised Operating Net Heat Rate | IF('General Information' Sr. No. 3 ="DG Set",H.1.2-H.2.1-H.2.2-D.7,"Not Applicable") | kcal/kwh | Not Applicable

## NF-1 Coal Quality
Normalization Factor for Fuel Quality in TPP
Name of the Thermal Power Station |  |  |  | 0
Documents Avaialbility |  |  |  | Yes | Yes
Sr No | Item | Basis/Calculation | Unit | Unit 1 |  |  | Unit 2 |  |  | Unit 3 |  |  | Unit 4 |  |  | Unit 5 |  |  | Unit 6 |  |  | Unit 7 |  |  | Unit 8 |  |  | Unit 9 |  |  | Unit 10
|  |  |  | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY
1 | Unit Capacity | As per Form Sh Sr. No. 4(i) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Turbine Heat Rate | IF('Form Sh' OEM THR [5.(i)]=0,'Form Sh' PG Test THR,'Form Sh' OEM THR [5.(i)]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Generation | As per Form Sh Sr. No. AY.[6.(i)] | MU | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
4 | Total Moisture | As per Form Sh Sr. No. 10.1.A.a.(iii) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Ash | As per Form Sh Sr. No. 10.1.A.a. (iv) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | GCV | As per Form Sh Sr. No. 10.1.A.a.(v) | kcal/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Hydrogen | As per Form Sh Sr. No. 10.1.A.b.(ii) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | % Boiler Efficiency (As per Formulae) | 92.5- {50*[3] +630*([2]+9*[5])}/[4] | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Actual Design Boiler Efficiency of Unit (As per OEM) | As per Form Sh | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | % Decrease in Efficiency from calculated Boiler operating Efficiency to calculated Boiler Design Efficiency | AY=(D[8]-AY[8])/D[8], BY=(D[8]-BY[8])/D[8] | % | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
11 | Degradation/Upgradation of Actual Boiler Design Efficiency | AY=D[9]*AY[10]/100, BY=D[9]*AY[10]/100 | % | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
12 | Normalised Design Boiler Efficiency for Unit | IFERROR(D[9])- AY[11], 0), | % | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
13 | Difference in Normalised Boiler Efficiency between BY and AY | [12] (BY) - [12](AY) | % | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
14 | Normalised Gross Heat Rate for AY | [D](2)*100/AY(12) | kcal/kWh | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
15 | Heat Rate to be normalised in the Unit operating Heat Rate | IF(AY[13]<0,0,[14]-D[2] x100/BY[18]) | kcal/kWh | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
16 | Heat Rate to be normalised in the station operating Heat Rate | (U#1(AY[15]*AY[3])+ U#2 ((AY[15]*AY[3])+ U#3 ((AY[15]*AY[3]) +U#4 ((AY[15]*AY[3]) + U#5 ((AY[15]*AY[3]) + U#6 ((AY[15]*AY[3]) + U#7 ((AY[15]*AY[3]) + U#8 ((AY[15]*AY[3]) + U#9 ((AY[15]*AY[3]) + U#10 ((AY[15]*AY[3]))/(U#1 (AY[3]) + U#2 (AY[3]) + U#3 (AY[3]) + U#4 (AY[3]) + U#5 (AY[3]) + U#6 (AY[3]) + U#7 (AY[3]) + U#8 (AY[3]) +U#9 (AY[3]) + U#10 (AY[3])) | kcal/kWh | 0
17 | Normalised Boiler Efficiency Design for Unit for the AY as compared to the BY | IFERROR(IF(AY[13]<=0,BY[9],D[9] - AY[13]),0) | % | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
18 | Normalised Boiler Efficiency Design for Station | (U#1 (AY[17]*D[1]) + U#2 (AY[17]*D[1]) +U#3 (AY[17]*D[1]) +U#4 (AY[17]*D[1]) +U#5 (AY[17]*D[1]) + U#6 (AY[17]*D[1]) + U#7 (AY[17]*D[1]) + U#8 (AY[17]*D[1]) +U#9 (AY[17]*D[1]) + U#10 (AY[17]*D[1]))/(U#1 (D[1]) + U#2 (D[1]) +U#3 (D[1]) +U#4 (D[1]) +U#5 (D[1]) + U#6 (D[1]) +U#7 (D[1]) +U#8 (D[1]) +U#9 (D[1]) +U#10 (D[1])) | % | 0
19 | Unit Design Gross Heat Rate |  | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Station Design Gross Heat Rate |  | kcal/kWh | 0 | 0 | 0
21 | Station Design Boiler Efficiency |  | % | 0 | 0 | 0

## NF-2 PLF
Normalization Factor for Unit/Module Load Factor
Name of the Thermal Power Station |  |  |  | 0
Documents Availability |  |  |  | Yes | Yes
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Unit-1 |  | Unit-2 |  | Unit-3 |  | Unit-4 |  | Unit-5 |  | Unit-6 |  | Unit-7 |  | Unit-8 |  | Unit-9 |  | Unit-10
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | Remarks
1 | Unit Capacity | NF-1 Coal Quality'! Sr No 1 for AY and 'NF-1 Coal Quality'!Sr 1 for BY | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Turbine Heat Rate @ 100% Load (OEM) | (IF(General Information' Sr. No. 3="Coal/Lignite/Oil/Gas Fired",IF('Form Sh' OEM THR =0,'Form Sh' PG Test THR,'Form Sh' OEM THR),860*100/AY[3], 0) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Boiler Design Efficiency | IF('Form Sh' OEM [B.Eff.]=0,'Form Sh' PG Test [B. Eff.],'Form Sh' OEM [B.Eff.]) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Design Turbine Heat Rate @ 100% Load (Curve or HBD) | As per 'Form Sh= U#1[5.(i)], U#2[5.(ii), U#2[5.(iii), U#2[5.(iv), U#2[5.(v), U#2[5.(vi), U#2[5.(vii), U#2[5.(viii), U#2[5.(ix), U#2[5.(x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | % Difference between Design Turbine/Module Heat Rate and Design Curve or HBD Turbine/Module Heat rate | IFERROR((AY[2] - AY[4])*100/AY[2],0) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Plant Availability Factor | U#1{'Form Sh'AY[12.2.(i)], 'Form Sh'BY[12.2.(i)]}, U#2{'Form Sh'AY[12.2.(ii)], 'Form Sh'BY[12.2.(ii)]}, U#3{'Form Sh'AY[12.2.(iii)], 'Form Sh'BY[12.2.(iii)]}, U#4{'Form Sh'AY[12.2.(iv)], 'Form Sh'BY[12.2.(iv)]}, U#5{'Form Sh'AY[12.2.(v)], 'Form Sh'BY[12.2.(v)]}, U#6{'Form Sh'AY[12.2.(vi)], 'Form Sh'BY[12.2.(vi)]}, U#7{'Form Sh'AY[12.2.(vii)], 'Form Sh'BY[12.2.(vii)]}, U#8{'Form Sh'AY[12.2.(viii)], 'Form Sh'BY[12.2.(viii)]}, U#9{'Form Sh'AY[12.2.(ix)], 'Form Sh'BY[12.2.(ix)]}, U#10{'Form Sh'AY[12.2.(x)], 'Form Sh'BY[12.2.(x)]} | Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
7 | Average Operating Load (MW) caused by low ULF/MLF due to external factor | U#1{'Form Sh'AY[12.2.(i)], 'Form Sh'BY[12.2.(i)]}, U#2{'Form Sh'AY[12.2.(ii)], 'Form Sh'BY[12.2.(ii)]}, U#3{'Form Sh'AY[12.2.(iii)], 'Form Sh'BY[12.2.(iii)]}, U#4{'Form Sh'AY[12.2.(iv)], 'Form Sh'BY[12.2.(iv)]}, U#5{'Form Sh'AY[12.2.(v)], 'Form Sh'BY[12.2.(v)]}, U#6{'Form Sh'AY[12.2.(vi)], 'Form Sh'BY[12.2.(vi)]}, U#7{'Form Sh'AY[12.2.(vii)], 'Form Sh'BY[12.2.(vii)]}, U#8{'Form Sh'AY[12.2.(viii)], 'Form Sh'BY[12.2.(viii)]}, U#9{'Form Sh'AY[12.2.(ix)], 'Form Sh'BY[12.2.(ix)]}, U#10{'Form Sh'AY[12.2.(x)], 'Form Sh'BY[12.2.(x)]} | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Average Operating hours at Low ULF/MLF | U#1{'Form Sh'AY[12.2.(i)], 'Form Sh'BY[12.2.(i)]}, U#2{'Form Sh'AY[12.2.(ii)], 'Form Sh'BY[12.2.(ii)]}, U#3{'Form Sh'AY[12.2.(iii)], 'Form Sh'BY[12.2.(iii)]}, U#4{'Form Sh'AY[12.2.(iv)], 'Form Sh'BY[12.2.(iv)]}, U#5{'Form Sh'AY[12.2.(v)], 'Form Sh'BY[12.2.(v)]}, U#6{'Form Sh'AY[12.2.(vi)], 'Form Sh'BY[12.2.(vi)]}, U#7{'Form Sh'AY[12.2.(vii)], 'Form Sh'BY[12.2.(vii)]}, U#8{'Form Sh'AY[12.2.(viii)], 'Form Sh'BY[12.2.(viii)]}, U#9{'Form Sh'AY[12.2.(ix)], 'Form Sh'BY[12.2.(ix)]}, U#10{'Form Sh'AY[12.2.(x)], 'Form Sh'BY[12.2.(x)]} | Hrs/Annum | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total Operating hours in year as per Unit Availability factor | AY= 8760*AY[6], BY=8760*BY[6] | Hrs/Annum | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
10 | Operating hours at full load | AY[9] - AY[8] | Hrs/Annum | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
11 | Loading Vs Heat Rate Equation | U#1='Form Sh'5.(i), U#2='Form Sh'5.(ii), U#3='Form Sh'5.(iii), U#4='Form Sh'5.(iv), U#5='Form Sh'5.(v), U#6='Form Sh'5.(vi), U#7='Form Sh'5.(vii), U#8='Form Sh'5.(viii), U#9='Form Sh'5.(ix), U#10='Form Sh'5.(x), | Quadratic Equation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Equation Constant 1 | U#1='Form Sh'5.(i), U#2='Form Sh'5.(ii), U#3='Form Sh'5.(iii), U#4='Form Sh'5.(iv), U#5='Form Sh'5.(v), U#6='Form Sh'5.(vi), U#7='Form Sh'5.(vii), U#8='Form Sh'5.(viii), U#9='Form Sh'5.(ix), U#10='Form Sh'5.(x), | a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Equation Constant 2 | U#1='Form Sh'5.(i), U#2='Form Sh'5.(ii), U#3='Form Sh'5.(iii), U#4='Form Sh'5.(iv), U#5='Form Sh'5.(v), U#6='Form Sh'5.(vi), U#7='Form Sh'5.(vii), U#8='Form Sh'5.(viii), U#9='Form Sh'5.(ix), U#10='Form Sh'5.(x), | b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Equation Constant 3 | U#1='Form Sh'5.(i), U#2='Form Sh'5.(ii), U#3='Form Sh'5.(iii), U#4='Form Sh'5.(iv), U#5='Form Sh'5.(v), U#6='Form Sh'5.(vi), U#7='Form Sh'5.(vii), U#8='Form Sh'5.(viii), U#9='Form Sh'5.(ix), U#10='Form Sh'5.(x), | c | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Turbine Heat Rate as per Load Vs Heat Rate Equation due to external factor | AY= AY[12]*AY[7]^2-AY[13]*AY[7]+AY[14], BY= BY[12]*BY[7]^2-BY[13]*BY[7]+BY[14] | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Design Turbine Heat Rate after Curve correction and difference correction | AY = AY[15]*(1+AY[5]/100), BY = BY[15]*(1+BY[5]/100) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Normalised Design Turbine Heat rate due to external factor | AY = IFERROR((E7*E15+E23*E13)/(E14),0) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Difference of Turbine Heat Rate due to external factor between AY and BY | AY[17]- BY[17] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
19 | Normalised Design Turbine Heat rate due to external factor as compared to BY | AY[2]+AY[18] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
20 | Normalised Designed Station Turbine Heat Rate due to ULF as comapred to BY |  | kcal/kWh | 0
Sr No | Item | Calculation | Unit | Assessment year[AY] | Baseline year[BY] | Remarks
21 | Weighted Design Turbine Heat Rate of Station |  | kcal/kWh | 0 | 0
22 | Normalised Design Station Turbine Heat Rate due to ULF as compared to BY | AY[20] | kcal/kWh | 0
23 | Station Boiler Efficiency |  | % | 0
24 | Heat rate to be normalised due to low Loading | (AY[22] -AY[21])*100/AY[23] | kcal/kWh | 0
∑_(𝑖=1)^10▒█(@𝐴𝑌[1]𝑋 𝐴𝑌[2]@)
∑_(𝑖=1)^10▒█(@𝐴𝑌[1]𝑋 𝐴𝑌[2]@)
∑_(𝑖=1)^10▒█(@𝐴𝑌[1]𝑋 𝐴𝑌[3" " ]@)

## NF-3 APC PLF
Normalization Factor for APC
Name of the Thermal Power Station |  | 0
Documents Availability |  |  |  | Yes | Yes
Sr No | Item | Calculation/Basis | Unit | Assessment Year (AY) | Baseline Year (BY) | Remarks
1 | Station Capacity | Form Sh' 7.(ii) | MW | 0 | 0
2 | APC | As per 'Form Sh' 7(vii) | % | 0 | 0
3 | APC Trend line Equation | As per 'Form Sh' 12.3.(i) |  | 0 | 0
4 | Constant 1 | As per 'Form Sh' 12.3.(i) | a | 0 | 0
5 | Constant 2 | As per 'Form Sh' 12.3.(i) | b | 0 | 0
6 | Constant 3 | As per 'Form Sh' 12.3.(i) | c | 0 | 0
7 | Plant Availability Factor | As per 'Form Sh' 7(iv) |  | 1 | 1
8 | Station Average Operating Load (MW) caused by low loading due to external factor | As per 'Form Sh' 12.2. (xi) | MW | 0 | 0
9 | Weighted Average Operating hours at Low loading due to external factor | As per 'Form Sh' 12.2. (xi) | hrs | 0 | 0
10 | Average Operating Load (MW) caused by low loading due to Internal factor | As per 'Form Sh' 12.2. (xi) | MW | 0 | 0
11 | Weighted Average Operating hours at Low loading due to internal factor | As per 'Form Sh' 12.2. (xi) | hrs | 0 | 0
12 | Operating hours at full Load | 8760*AY[7] - AY[9] - AY[11] | hrs | 8760 | 8760
13 | Weighted Operating Station Load | (AY[1]*AY[12] + AY[8]*AY[9] + AY[10]*AY[11]/(AY[9] + AY[11] +AY[12]) | MW | 0 | 0
14 | Actual Loading Factor | AY[13]*100/AY[1] | % | 0 | 0
15 | Weighted Station Load without internal factor | (AY[8]*AY[9] + AY[1]* AY[12] + AY[1]*AY[11])/(AY[9] + AY[11] +AY[12]) | MW | 0 | 0
16 | Normalised Loading Factor | AY[15]*100/AY[1] | % | 0 | 0
17 | % APC as per trend line | AY= - AY[4]*AY[16]^2- AY[5]*AY[16] + AY[6] | % | 0 | 0
18 | Difference in APC | AY[17]-BY[17] | % | 0
19 | Normalised APC | IF(AY[18]<0,AY[2],AY[2] - AY[18]) | % | 0

## NF-3.1 APC CQ
Normalization Factor for Primary Air Fan Loading due to Coal Quality
Name of the Thermal Power Station |  |  | 0
Documentation Availability |  |  |  | Yes | Yes
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Unit-1 |  | Unit-2 |  | Unit-3 |  | Unit-4 |  | Unit-5 |  | Unit-6 |  | Unit-7 |  | Unit-8 |  | Unit-9 |  | Unit-10 |  | Remarks
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY
1 | Gross Heat Rate | Form Sh'! (6) UGHR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Operating Load | Form Sh'! (6) Operating Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Gross Generation | Form Sh'! (6) Gross Generation | Million Units | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Operating Hours | (3)*1000/(2) | hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Coal GCV | Form Sh'! (A to J) 10.1 A a(v) | kcal/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Total Coal Consumption | (1)*(2)/(5) | Tonnes/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Normalised Total Coal Consumption | (6)BY*(5)BY/(%)AY | Tonnes/hr | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
8 | Increase in coal consumption due to change in GCV of coal in AY | (7)AY-(6)BY | Tonnes/hr | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
9 | Total Primary Air requirement per tonne of coal trendline equation | y = 6.0487x^-0.2055 Where x=Operating Load | Tonnes |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055 |  | y = 6.0487x-0.2055
10 | Total Primary Air requirement per tonne of coal trendline equation for BY and AY | y = 6.0487* (2)^-0.2055 | Tonnes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Total Primary Air requirement | (7)AY*(10)AY (6)BY*(10)BY | Tonnes/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Volume of Primary Air | (11)*1000/1.2333 | m³/ hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Power Consumption from PA fans | {2.275*(12)*900}/(0/95*0.8*10^6) | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Increase in energy consumption due to change in GCV of coal in AY | (13)AY-(13)BY | kW/Hr | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
15 | Normalized Thermal Energy due to change in GCV of coal | (14)AY*(1)AY*(4)AY/10^6 | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
16 | Normalization for station due to change in GCV of coal | (15)U#1+(15)U#2+(15)U#3+(15)U#4+(15)U#5+(15)U#6+(15)U#7+(15)U#8+(15)U#9+(15)U#10 | Million kcal | 0

## NF-3.2 APC CQ
Normalization Factor for Coal Mill, ID Fan & Ash Handling Plant Loading due to Coal Quality
Name of the Thermal Power Station |  |  | 0
Documentation Availability |  |  |  | Yes | Yes
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Unit-1 |  | Unit-2 |  | Unit-3 |  | Unit-4 |  | Unit-5 |  | Unit-6 |  | Unit-7 |  | Unit-8 |  | Unit-9 |  | Unit-10
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | Remarks
1 | Gross Heat Rate | Form Sh'! (6) UGHR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Operating Load | Form Sh'! (6) Operating Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Gross Generation | Form Sh'! (6) Gross Generation | Million Units | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Operating Hours | (3)*1000/(2) | hrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Coal GCV | Form Sh'! (A to J) 10.1 A a(v) | kcal/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Total Coal Consumption | (1)*(2)/(5) | Tonnes/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Total Electrical Energy consumption for Coal Grinding mills (VRM/Ball), ID Fan and Ash Handling Plant | form Sh'! A to J (d) AY & BY | Million Units | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Normalised Coal Consumption | (6)BY*(5)BY/(5)AY | Tonnes/hr | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
9 | Increase in coal consumption due to change in GCV of coal in AY | (8)AY-(8)BY | Tonnes/hr | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
10 | Total Electrical Energy consumption for Coal Grinding mills (VRM/Ball) per hour | (7)*10^6/(4) | kW/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Specific energy consumption per tonne of coal | (10)/(6) | kWh/Tonne | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Increase in energy consumption due to change in GCV of coal in AY | (9)*(11) | kW/hr | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
13 | Normalization due to change in GCV of coal | (12)*(1)*(4) | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
14 | Normalization for station due to change in GCV of coal | (13)U#1+(13)U#2+(13)U#3+(13)U#4+(13)U#5+(13)U#6+(13)U#7+(13)U#8+(13)U#9+(13)U#10 | Million kcal | 0

## NF-4 Gas Fuel Mix
Normalization Factor for Fuel Mix in Gas based Power Station
Name of the Thermal Power Station |  |  |  | 0
Documentation Availability |  |  |  | Yes | Yes
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Module-1 |  | Module-2 |  | Module-3 |  | Module-4 |  | Module-5 |  | Module-6 |  | Module-7 |  | Module-8 |  | Module-9 |  | Module-10
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | Remarks
1 | Unit Capacity | As per 'Form Sh' 5 (i) to 5 (x) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Module Heat Rate @ 100% Load (OEM) for Gas | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Design Module Heat Rate @ 100% Load for Naphtha | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Design Module Heat Rate @ 100% Load (OEM) for Oil/Other Fuel | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Actual Gross Generation from Gas | Form Sh' 7.1.(i) [OC-Gas]+ 'Form Sh' 7.1.(i)[CYI-Gas]+'Form Sh' 7.(i)[OCE-Gas] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Actual Gross Generation from Naphtha | Form Sh' 7.1.(i) [OC-Naphtha]+ 'Form Sh' 7.1.(i)[CYI-Naphtha]+'Form Sh' 7.(i)[OCE-Naphtha] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Actual Gross Generation from Oil/Other Fuel | Form Sh' 7.1.(i) [OC-Oil/Other Fuel]+ 'Form Sh' 7.1.(i)[CYI-Oil/Other Fuel]+'Form Sh' 7.(i)[OCE-Oil/Other Fuel] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Gross Generation from Fuel Mix | [5] + [6] + [7] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Module Heat Rate with Fuel Mix | ([2]*[5]+[3]*[6]+[4]*[7])/([5] + [6] + [7]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Difference in Assessment year w.r.t. Baseline Year | AY[9] - BY[9] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11 | Notional energy for Fuel Mix to be Normalised for Module | [10]*[8] | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12 | Notional energy for Fuel Mix to be Normalised for station | M1[12] + M2[12] +….. | Million kcal | 0

## NF-5 Gas OC Cycle
Normalization Factor for Open and Closed cycle operation in Gas based Power Station
Name of the Thermal Power Station |  |  |  | 0
Documentation Availability |  |  |  | Yes | Yes
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Module-1 |  | Module-2 |  | Module-3 |  | Module-4 |  | Module-5 |  | Module-6 |  | Module-7 |  | Module-8 |  | Module-9 |  | Module-10
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | Remarks
1 | Unit Capacity | As per 'Form Sh' 5. (i) to 5. (x) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Module Heat Rate @ 100% Load (OEM) for Closed Cycle | IF('Form Sh' OEM UHR [5.(I)] =0,'Form Sh' PG Test UHR [5.(I)],'Form Sh' OEM UHR [5.(I)]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Design Module Heat Rate @ 100% Load for Open Cycle | Form Sh' 5.(i) DHR at Different Condition [OC-MHR] | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Design Module Heat Rate @ 100% Load (OEM) for Oil/Other Fuel | Form Sh' 5.(i) DHR at Different Condition [Oil/Other Fuel - MHR] | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Actual Gross Generation during Closed Cycle | SUM('Form Sh' 7.1 (i) [CC-(Gas+ Naphtha + Oil/Others)] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Actual Gross Generation during Open Cycle due to external factor | SUM('Form Sh' 7.1 (i) [OCE-(Gas+ Naphtha + Oil/Others)] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Actual Gross Generation during Open Cycle due to internal factor | SUM('Form Sh' 7.1 (i) [OCI-(Gas+ Naphtha + Oil/Others)] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Gross Generation during Open Cycle (External Factor) and Closed Cycle operation | [10] + [11] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Module Heat Rate for Open and Closed Cycle Operation | ([2]*[5]+ [3]*[6]/([5] + [6]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Difference in Assessment year w.r.t. Baseline Year | AY[9] -BY[9] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11 | Notion energy for Gas OC Cycle to be Normalised for Module | [10] * [8] | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12 | Notion energy for Gas OC Cycle to be Normalised for station | M1[11] + M2 [11] + ………… | Million kcal | 0

## NF-6 Gas NCV
Normalization Factor for Gas Quality in Gas based Power Station
Name of the Thermal Power Station |  | 0
Documentation Availability |  |  |  | Yes | Yes
Type of Thermal Power Plant |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | AY | BY
1 | Station Net Heat Rate (NHR) | Form Sh'! 7 (ix) AY & BY | kcal/kWh | 0 | 0
2 | Net Calorific Value of Gas | Form Sh'! 10.2.1 (xii) AY & BY | kcal/kg | 0 | 0
3 | NHR trendline equation | y = -10^-7x^2 + 0.0051x + 1490.5 | kcal/kWh | y = -10^-7x^2 + 0.0051x + 1490.5 | y = -10^-7x^2 + 0.0051x + 1490.5
4 | NHR as per trendline equation | y = -10^-7x^2 + 0.0051x + 1490.5 Where x=NCV | kcal/kWh | 1490.5 | 1490.5
5 | Difference in NHR as per trendlne Equation between AY and BY | (4)AY-(4)BY | kcal/kWh | 0
6 | Gross Generation in AY | Form Sh'! 6.1 Gr. Gen AY | Million Units | 0
7 | Normalization due to change in Gas Quality | (6)*(5) | Million Kcal | 0

## NF-7 Others
Normalization -Others (Startup/Shutdown/Environmental Concern)
Name of the Thermal Power Station |  | 0
Sr No | Unit | Calculation/Basis | MW | Baseline Year (BY) |  |  | Assessment Year (AY) |  |  | Difference (AY)-(BY) |  |  | kL Oil consumption |  |  | Remarks
|  |  |  | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start
1 | Unit 1 | Form Sh'! 12.4 c(i) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Unit 2 | Form Sh'! 12.4 c(ii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Unit 3 | Form Sh'! 12.4 c(iii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Unit 4 | Form Sh'! 12.4 c(iv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Unit 5 | Form Sh'! 12.4 c(v) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Unit 6 | Form Sh'! 12.4 c(vi) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Unit 7 | Form Sh'! 12.4 c(vii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Unit 8 | Form Sh'! 12.4 c(viii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Unit 9 | Form Sh'! 12.4 c(ix) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Unit 10 | Form Sh'! 12.4 c(x) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0
Documentation Availability |  |  |  | Yes | Yes
Sr No | Item | Calculation/Basis | Unit | Assessment Year (AY) | Baseline Year (BY) | Remarks
12 | Thermal Energy to be subtracted due to Cold/Warm/Hot Start up (External Factor) | (11CS+11WS+11HS)*10 | Million kcal | 0
13 | Electrical Energy to be subtracted due to Shutdown (External Factor) | Form Sh'! 12.4 B(i) | MU | 0 | 0
14 | Electrical Energy to be subtracted due to Environmental concern (External Factor) | Form Sh'! 12.5 Total Ad.El.En.Con. | MU | 0
15 | Thermal Energy to be subtracted due to Environmental concern (External Factor) | Form Sh'12.5 Total Ad.Th.En.Con. | Million kcal | 0
16 | Electrical Energy to be subtracted due to Unforeseen Circumstances (External Factor) | Form Sh'! 12.6 (i) | MU | 0 | 0
17 | Thermal Energy to be subtracted due to Unforeseen Circumstances (External Factor) | Form Sh'! 12.6 (ii) | Million kcal | 0 | 0
18 | Gross Heat Rate of Station | Form Sh'! 6.1 UGHR | kcal/kWh | 0 | 0
19 | Total Electrical Energy | AY={(13AY)+914AY)+(16AY)}*(18AY) BY={(13BY)+(16BY)}*(18BY) | Million kcal | 0 | 0
20 | Total Thermal Energy | AY=(15AY)+(17AY)+(12AY) BY=(17BY) | Million kcal | 0 | 0
21 | Total Energy to be subtracted | {(19AY)+(20AY)}-{(19BY)+(20BY)} | Million kcal | 0

## Annex PLF
Turbine Heat Rate Vs Load
% Load | Gross Load (MW) | Heat Rate | Heat Rate as per Equation
% | MW | (kcal/kWh) | (kcal/kwh)
30.2857 | 63.6 | 2327.75 | 2333.2697
35.7143 | 75 | 2292.6 | 2284.92
47.619 | 100 | 2196 | 2194.36
59.5238 | 125 | 2116.65 | 2125.05
71.4286 | 150 | 2074.05 | 2076.99
83.3333 | 175 | 2057.4 | 2050.18
86.1905 | 181 | 2052 | 2046.9076
95.2381 | 200 | 2042.6 | 2044.62
100 | 210 | 2044.44 | 2048.346
12600

## Annex APC
200*3+500*4 mw Station (1st Oct’13-31 Dec’13)

## NF-8 Fuel Mix for TPP
Normalization Factor for Fuel Mix inThermal Power Station
Name of the Thermal Power Station |  | 0
Type of Thermal Power Plant |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Unit-1 |  | Unit-2 |  | Unit-3 |  | Unit-4 |  | Unit-5 |  | Remarks
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY
1 | Unit Capacity | As per 'Form Sh' 5 (i) to 5 (x) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Gross Heat Rate @ 100% Load (OEM) from Fuel 1 (Gas) | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Design Gross Heat Rate @ 100% Load from fuel 2 (Oil/others) | As per 'Form Sh' 5.2 (i) to 5.2 (v) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Actual Gross Generation from Fuel 1 (Gas) | Form Sh' 7.1.(i) [OC-Gas]+ 'Form Sh' 7.1.(i)[CYI-Gas]+'Form Sh' 7.(i)[OCE-Gas] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Actual Gross Generation from Fuel 2 (Oil/ Others) | Form Sh' 7.1.(i) [Oil/others]+ 'Form Sh' 7.1.(i)[CYIOil/others]+'Form Sh' 7.(i)[Oil/others] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
s
6 | Gross Generation from Fuel Mix | [4] + [5] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Gross Heat Rate with Fuel Mix | ([2]*[4]+[3]*[5])/([4] + [5]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Difference in Assessment year w.r.t. Baseline Year | AY[7] - BY[7] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0
9 | Notional energy for Fuel Mix to be Normalised for Module | [9]*[6] | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0
10 | Notional energy for Fuel Mix to be Normalised for station | M1[9] + M2[9] +….. | Million kcal | 0